## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | ORIFICE ASSEMBLY | [5 empty] | DS-IN-F-003A
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
ORIFICE ASSEMBLY
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | MAY.24.'18 |  |  | FOR QUOTAION |  | J.H Jung |  | C.M Lee | K.Y Noh |  |  | H.D Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-003A |  |  | 2018.05.24

## Orifice
[5 empty] | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT
[18 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem
[18 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO.
| JOB NO. |  | : M0556 |  | ORIFICE ASSEMBLY | [12 empty] | DS-IN-F-003A |  |  |  | ORIFICE ASSEMBLY | [12 empty] | DS-IN-F-003A |  |  |  | ORIFICE ASSEMBLY | [12 empty] | DS-IN-F-003A |  |  |  | ORIFICE ASSEMBLY | [12 empty] | DS-IN-F-003A |  |  |  | ORIFICE ASSEMBLY | [12 empty] | DS-IN-F-003A
| PROJECT NAME |  | : IPA 50KTA Exp. | [14 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [14 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A
1 | GENERAL | Tag No. |  |  | FE-1119 |  |  |  |  | FE-1128 |  |  |  | FE-1141 |  |  |  | FE-1142 |  |  |  | FE-1151 |  |  |  |  | FE-1165 |  |  |  | FE-1168 |  |  |  | FE-1311 |  |  |  | FE-1320 |  |  |  |  | FE-1321 |  |  |  | FE-1331 |  |  |  | FE-1335 |  |  |  | FE-1351 |  |  |  |  | FE-1352 |  |  |  | FE-1801 |  |  |  | FE-1811 |  |  |  | FE-1812 |  |  |  |  | FE-1813 |  |  |  | FE-1821 | [6 empty] | 19
2 |  | P&ID No. |  |  | D-1-IPA-1001 |  |  |  |  | D-1-IPA-1001 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1002 |  |  |  |  | D-1-IPA-1003 |  |  |  | D-1-IPA-1003 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3002 |  |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3004 |  |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8012
3 |  | Service |  |  | HP STEAM TO EA-110 |  |  |  |  | PPF TO EA-112 |  |  |  | GB-120 DISCHARGE |  |  |  | GB-120 SUCTION |  |  |  | EA-140A/B WCS |  |  |  |  | EA-165 WCS |  |  |  | FC-170 FEED INLET |  |  |  | SM TO EA-311 |  |  |  | DA-320 FEED INLET |  |  |  |  | SM TO EA-321 |  |  |  | SL TO EA-331 |  |  |  | DA-330 OVHD TO DA-320 |  |  |  | DA-320 OVHD TO EA-351A/B |  |  |  |  | SM TO EA-352 |  |  |  | HS STEAM FORM B.L |  |  |  | SH TO CONSUMERS |  |  |  | SM TO CONSUMERS |  |  |  |  | SL TO CONSUMERS |  |  |  | WR TO EF-820
4 |  | Line Class |  |  | BA59C |  |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BB55C |  |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  | BB57C |  |  |  | BB55C1 |  |  |  |  | BB57C |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  |  | BB57C |  |  |  | BA59C |  |  |  | BA59C |  |  |  | BB57C |  |  |  |  | BB55C |  |  |  | BB55C
5 |  | Line Size |  | Line Schedule | 6" |  |  |  |  | 2" |  |  |  | 10" |  |  |  | 12" |  |  |  | 8" |  |  |  |  | 6" |  |  |  | 6" |  |  |  | 6" |  |  |  | 6" |  |  |  |  | 8" |  |  |  | 6" |  |  |  | 6" |  |  |  | 12" |  |  |  |  | 6" |  |  |  | 6" |  |  |  | 6" |  |  |  | 10" |  |  |  |  | 6" |  |  |  | 6"
6 |  | Nace Requirement
7 |  | Enclosure Class
8 |  | Application Code |  |  | ISO 5167 |  |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  | ISO 5167 |  |  |  |  | ISO 5167 |  |  |  | ISO 5167
9 | SERVICE CONDITION | Fluid |  |  | SH |  |  |  |  | PPF |  |  |  | PRG |  |  |  | PRG |  |  |  | WCS |  |  |  |  | WCS |  |  |  | PRG |  |  |  | SM |  |  |  | PDI |  |  |  |  | SM |  |  |  | SL |  |  |  | PDI |  |  |  | PDI |  |  |  |  | SM |  |  |  | HS |  |  |  | SH |  |  |  | SM |  |  |  |  | SL |  |  |  | WR
10 |  | Flow Rate Unit |  | State | kg/h |  |  |  | S | m3/h |  |  | L | kg/h |  |  | V | kg/h |  |  | V | m3/h |  |  |  | L | m3/h |  |  | L | kg/h |  |  | V | kg/h |  |  | S | m3/h |  |  |  | L | kg/h |  |  | S | kg/h |  |  | S | kg/h |  |  | V | kg/h |  |  |  | V | kg/h |  |  | S | kg/h |  |  | S | kg/h |  |  | S | kg/h |  |  |  | S | kg/h |  |  | S | m3/h |  |  | L
11 |  |  |  |  | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN
12 |  | Flow Rate |  |  | 7011.6 |  | 5843 |  | - | 10.704 | 8.92 |  | - | 223101.15 | 194001 |  | - | 125811.15 | 109401 |  | - | 313.4998 |  | 261.2499 |  | - | 62.1691 | 51.8076 |  | - | 1342.26 | 1118.55 |  | - | 3631.2 | 3026 |  | - | 132.0756 |  | 110.063 |  | - | 13024.8 | 10854 |  | - | 1806 | 1505 |  | - | 4252.5 | 3543.75 |  | - | 24554.04 |  | 20461.7 |  | - | 4800 | 587 |  | - | 26965 | 19810 |  | - | 7352 | 6214 |  | - | 21930 |  | 15599.1 |  | - | 2827 | 2565.862 |  | - | 41.8169 | 30.7602 |  | -
13 |  | Inlet Pressure |  | (kg/cm2g) | - |  | 31 |  | - | - | 49.35 |  | - | - | 47 |  | - | - | 31 |  | - | - |  | 5 |  | - | - | 5 |  | - | - | 0.1 |  | - | - | 9.8 |  | - | - |  | 5.54 |  | - | - | 9.8 |  | - | - | 3.5 |  | - | - | 1.9 |  | - | - |  | 1.6 |  | - | - | 9.8 |  | - | - | 40 |  | - | - | 31 |  | - | - |  | 9.8 |  | - | - | 3.5 |  | - | - | 4 |  | -
14 |  | Temperature |  | (deg C) | - |  | 255 |  | - | - | 25 |  | - | - | 125 |  | - | - | 93.94 |  | - | - |  | 32 |  | - | - | 32 |  | - | - | 38 |  | - | - | 198 |  | - | - |  | 97.17 |  | - | - | 198 |  | - | - | 147 |  | - | - | 110.9 |  | - | - |  | 105.62 |  | - | - | 198 |  | - | - | 340 |  | - | - | 255 |  | - | - |  | 198 |  | - | - | 165 |  | - | - | AMB |  | -
15 |  | S.G. @ Op |  | Density @ Op |  |  |  | 14.2 |  |  |  | 507.17 |  |  |  | 90.02 |  |  |  | 66.39 |  |  |  |  | 995.3 |  |  |  | 995.3 |  |  |  | 1.95 |  |  |  | 5.0955 |  |  |  |  | 903.64 |  |  |  | 5.0955 |  |  |  | 1.9 |  |  |  | 3.83 |  |  |  |  | 3.98 |  |  |  | 5.0955 |  |  |  | 15.481 |  |  |  | 14.7 |  |  |  |  | 5.208 |  |  |  | 2.274 |  |  |  | 998.4
16 |  | Viscosity @ Op. |  | Molcular Mass | 0.019 |  |  | 18 |  | 0.0803 |  | - |  | 0.0143 |  | 43.87 |  | 0.0127 |  | 43.87 |  | 0.764 |  |  | - |  | 0.764 |  | - |  | 0.0088 |  | 44.71 |  | 0.016 |  | 18 |  | 0.2899 |  |  | - |  | 0.016 |  | 18 |  | 0.014 |  | 18 |  | 0.011662 |  | 41.139 |  | 0.011 |  |  | 46.92 |  | 0.016 |  | 18 |  | 0.02 |  | 18 |  | 0.733 |  | 18 |  | 0.622 |  |  | 18 |  | 0.622 |  | 18 |  | 1 |  | -
17 |  | Specific Heat Ratio |  | Comp. Factor (Z) | 1.1496 |  |  | 0.9073 |  | - |  | - |  | 1.65 |  | 0.66 |  | 1.57 |  | 0.68 |  | - |  |  | - |  | - |  | - |  | 1.14 |  | 0.98 |  | 1.357 |  | 0.9588 |  | - |  |  | - |  | 1.357 |  | 0.9588 |  | 1.34 |  | 0.79696 |  | 1.14 |  | 0.97 |  | 1.12 |  |  | 0.97 |  | 1.357 |  | 0.9588 |  | 1.413 |  | 0.99746 |  | 1.5 |  | 1 |  | 1.3957 |  |  | 1 |  | 1.3566 |  | 1 |  | - |  | -
18 |  | Max. Allowable Pressure Drop (kg/cm2g) |  |  | 0.5 |  |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  |  | 0.5 |  |  |  | 0.5
19
20 | ORIFICE PLATES | Type |  |  | CONCENTRIC |  |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC |  |  |  |  | CONCENTRIC |  |  |  | CONCENTRIC
21 |  | Material |  |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS
22 |  | Thickness |  |  | 3 mm |  |  |  |  | 3 mm |  |  |  | 6 mm |  |  |  | 6 mm |  |  |  | 3 mm |  |  |  |  | 3 mm |  |  |  | 3 mm |  |  |  | 3 mm |  |  |  | 3 mm |  |  |  |  | 3 mm |  |  |  | 3 mm |  |  |  | 3 mm |  |  |  | 6 mm |  |  |  |  | 3 mm |  |  |  | 3 mm |  |  |  | 3 mm |  |  |  | 6 mm |  |  |  |  | 3 mm |  |  |  | 3 mm
23 |  | Bore Diameter |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | *
24 |  | Beta Ratio |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | *
25 |  | Drain or Vent Hole |  |  | DRAIN |  |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  | DRAIN |  |  |  |  | DRAIN |  |  |  | DRAIN
26 |  | Flow Full Scale |  |  | 0 ~ 9000 |  |  |  |  | 0 ~ 15 |  |  |  | 0 ~ 250000 |  |  |  | 0 ~ 150000 |  |  |  | 0 ~ 400 |  |  |  |  | 0 ~ 80 |  |  |  | 0 ~ 1500 |  |  |  | 0 ~ 4500 |  |  |  | 0 ~ 150 |  |  |  |  | 0 ~ 15000 |  |  |  | 0 ~ 2000 |  |  |  | 0 ~ 5000 |  |  |  | 0 ~ 30000 |  |  |  |  | 0 ~ 5000 |  |  |  | 0 ~ 30000 |  |  |  | 0 ~ 9000 |  |  |  | 0 ~ 25000 |  |  |  |  | 0 ~ 4000 |  |  |  | 0 ~ 45
27 |  | Differential Pressure @ Full Scale |  |  | 2500 mmH2O |  |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O
28
29
30 | ORIFICE FLANGES | Flange Size & Rating (ANSI) |  |  | 6" 600# RF |  |  |  |  | 2" 600# RF |  |  |  | 10" 600# RF |  |  |  | 12" 600# RF |  |  |  | 8" 300# RF |  |  |  |  | 6" 300# RF |  |  |  | 6" 300# RF |  |  |  | 6" 300# RF |  |  |  | 6" 300# RF |  |  |  |  | 8" 300# RF |  |  |  | 6" 300# RF |  |  |  | 6" 300# RF |  |  |  | 12" 300# RF |  |  |  |  | 6" 300# RF |  |  |  | 6" 600# RF |  |  |  | 6" 600# RF |  |  |  | 10" 300# RF |  |  |  |  | 6" 300# RF |  |  |  | 6" 300# RF
31 |  | Flange Type |  |  | WELDING NECK |  |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  | WELDING NECK |  |  |  |  | WELDING NECK |  |  |  | WELDING NECK
32 |  |  | Flange |  | A105 |  |  |  |  | A105 |  |  |  | A105 |  |  |  | A105 |  |  |  | A105 |  |  |  |  | A105 |  |  |  | A105 |  |  |  | A105 |  |  |  | A105 |  |  |  |  | A105 |  |  |  | A105 |  |  |  | A105 |  |  |  | A105 |  |  |  |  | A105 |  |  |  | A105 |  |  |  | A105 |  |  |  | A105 |  |  |  |  | A105 |  |  |  | A105
33 |  | Material | Gasket |  | NOTE 4 |  |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  | NOTE 4 |  |  |  |  | NOTE 4 |  |  |  | NOTE 4
34 |  |  | Bolts & Nuts |  | A193 B7 / A194 2H |  |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H |  |  |  |  | A193 B7 / A194 2H |  |  |  | A193 B7 / A194 2H
35 |  |  | Jack Screw & Plug |  | 304SS |  |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105 |  | 304SS |  |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105 |  | 304SS |  |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105 |  | 304SS |  |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105 |  | 304SS |  |  | A105 |  | 304SS |  | A105 |  | 304SS |  | A105
36 |  | Taps Type |  |  | FLANGE TAP |  |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP |  |  |  |  | FLANGE TAP |  |  |  | FLANGE TAP
37 |  | Taps Size |  |  | 1/2" NPT |  |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT
38 |  | Taps Orientation
39 |  | Taps Nipple Type |  |  | S TYPE |  |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  | S TYPE |  |  |  |  | S TYPE |  |  |  | S TYPE
40 |  | Taps Valve |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES
41
42 | PROQ. | Manufacturer
43 |  | Model
44
45
[6 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE
[6 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor.
[6 empty] | 2. | Flange, nipple & tap valves shall be welded. | [15 empty] | 2. | Flange, nipple & tap valves shall be welded. | [15 empty] | 2. | Flange, nipple & tap valves shall be welded. | [15 empty] | 2. | Flange, nipple & tap valves shall be welded. | [15 empty] | 2. | Flange, nipple & tap valves shall be welded.
[6 empty] | 3. | Connection to instrument of tap valves shall be 1/2" NPT female. | [15 empty] | 3. | Connection to instrument of tap valves shall be 1/2" NPT female. | [15 empty] | 3. | Connection to instrument of tap valves shall be 1/2" NPT female. | [15 empty] | 3. | Connection to instrument of tap valves shall be 1/2" NPT female. | [15 empty] | 3. | Connection to instrument of tap valves shall be 1/2" NPT female.
[6 empty] | 4. | Gasket (Reffer to Line Class) | [15 empty] | 4. | Gasket (Reffer to Line Class) | [15 empty] | 4. | Gasket (Reffer to Line Class) | [15 empty] | 4. | Gasket (Reffer to Line Class) | [15 empty] | 4. | Gasket (Reffer to Line Class)
[7 empty] | BA59C |  | : 600# RF SPIRAL WOUND 304SS/GRAPHITE, 4.5T | [14 empty] | BA59C |  | : 600# RF SPIRAL WOUND 304SS/GRAPHITE, 4.5T | [14 empty] | BA59C |  | : 600# RF SPIRAL WOUND 304SS/GRAPHITE, 4.5T | [14 empty] | BA59C |  | : 600# RF SPIRAL WOUND 304SS/GRAPHITE, 4.5T | [14 empty] | BA59C |  | : 600# RF SPIRAL WOUND 304SS/GRAPHITE, 4.5T
[7 empty] | BB55C |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB55C |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB55C |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB55C |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB55C |  | : 300# RF NON-ASBESTOS SHEET, 1.6T
[7 empty] | BB55C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB55C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB55C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB55C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB55C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T
[7 empty] | BB57C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB57C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB57C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB57C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T | [14 empty] | BB57C1 |  | : 300# RF NON-ASBESTOS SHEET, 1.6T
[7 empty] | BB59C1 |  | : 600# RF SPIRAL WOUND/INNER RING F304, 4.5T | [14 empty] | BB59C1 |  | : 600# RF SPIRAL WOUND/INNER RING F304, 4.5T | [14 empty] | BB59C1 |  | : 600# RF SPIRAL WOUND/INNER RING F304, 4.5T | [14 empty] | BB59C1 |  | : 600# RF SPIRAL WOUND/INNER RING F304, 4.5T | [14 empty] | BB59C1 |  | : 600# RF SPIRAL WOUND/INNER RING F304, 4.5T