## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | MAGNETIC FLOWMETER | [5 empty] | DS-IN-F-004
| PROJECT NAME |  |  | : IPA Project | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | B
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA Project
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
MAGNETIC FLOWMETER
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
B |  | JUL.27.'18 |  |  | FOR QUOTAION |  | J.H Jung |  | C.M Lee | K.Y Noh |  |  | H.D Yoon
A |  | MAY.24.'18 |  |  | FOR QUOTAION |  | J.H Jung |  | C.M Lee | K.Y Noh |  |  | H.D Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-006 |  |  | 2018.07.27

## Magnetic
[6 empty] | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT
[19 empty] | LG Chem | [16 empty] | LG Chem
[19 empty] | DOC. NO. | [16 empty] | DOC. NO.
| JOB NO. |  | : M0556 |  |  | MAGNETIC FLOWMETER | [12 empty] | DS-IN-F-004 |  |  |  | MAGNETIC FLOWMETER | [12 empty] | DS-IN-F-004
| PROJECT NAME |  | : IPA Project | [15 empty] | REV. NO. | [16 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [15 empty] | B | [16 empty] | B
1 | GENERAL | Tag No. |  |  |  | FT-1314 |  |  |  |  | FT-1336 |  |  |  | FT-1355 |  |  |  | FT-1821 |  |  |  | FT-1839 |  |  |  |  | FT-1880 |  |  |  | FT-1890 | [6 empty] | 7
2 |  | P&ID No. |  |  |  | D-1-IPA-3001 |  |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-8012 |  |  |  | D-1-IPA-8013 |  |  |  |  | D-1-IPA-8022 |  |  |  | D-1-IPA-8024
3 |  | Service |  |  |  | PWW TO DA-310 |  |  |  |  | EA-324 OUTLET |  |  |  | FA-354 OUTLET |  |  |  | WR TO EF-820 |  |  |  | WT TO FB-835 |  |  |  |  | FILTERED WATER FROM BL |  |  |  | WW FROM EA-324
4 |  | Line Class |  |  |  | BB55C1 |  |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  |  | BB55C |  |  |  | BB55C1
5 |  | Line Size |  | Line Schedule |  | 4" |  |  |  |  | 3" |  |  |  | 1" |  |  |  | 4" |  |  |  | 3" |  |  |  |  | 4" |  |  |  | 3"
6 |  | Nace Requirement
7 |  | Enclosure Class |  |  |  | Ex d IIB T4, IP 56 |  |  |  |  | Ex d IIB T4, IP 56 |  |  |  | Ex d IIB T4, IP 56 |  |  |  | Ex d IIB T4, IP 56 |  |  |  | Ex d IIB T4, IP 56 |  |  |  |  | Ex d IIB T4, IP 56 |  |  |  | Ex d IIB T4, IP 56
8
9 | SERVICE CONDITION | Fluid |  |  |  | PWW |  |  |  |  | WW |  |  |  | PS |  |  |  | WR |  |  |  | WT |  |  |  |  | WR |  |  |  | WW
10 |  | Flow Rate Unit |  | State |  | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L
11 | [5 empty] | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN
12 |  | Flow Rate |  |  |  | 57.8 |  | 48.2 |  | - | 46 | 14 |  | - | 1.2 | - |  | - | 41.8 | 30.8 |  | - | 18.9 |  | 15.8 |  | - | 41.9 | 30.8 |  | - | 16.8 | 14 |  | -
13 |  | Inlet Pressure |  | (kg/cm2g) |  | - |  | 4 |  | - | - | 4.19 |  | - | - | 0.5 |  | - | - | 4 |  | - | - |  | 5 |  | - | - | 4 |  | - | - | 7 |  | -
14 |  | Temperature |  | (deg C) |  | - |  | 95 |  | - | - | 40 |  | - | - | 30 |  | - | - | AMB |  | - | - |  | AMB |  | - | - | AMB |  | - | - | 40 |  | -
16 |  | S.G. @ Op |  | Density @ Op |  |  |  |  | 962.1 |  |  |  | 992.5 |  |  |  | 802.1 |  |  |  | 998.4 |  |  |  |  | 997.3 |  |  |  | 997.3 |  |  |  | 992.5
17 |  | Viscosity @ Op. |  | Molcular Mass |  | 0.29 |  |  | - |  | 0.65 |  | - |  | 0.73 |  | - |  | 1 |  | - |  | 0.89 |  |  | - |  | 0.9 |  | - |  | 0.65 |  | -
18 |  | Max. Allowable Pressure Drop |  |  | (kg/cm2g) | 0.2 |  |  |  |  | 0.2 |  |  |  | 0.2 |  |  |  | 0.2 |  |  |  | 0.2 |  |  |  |  | 0.2 |  |  |  | 0.2
|  | Fluid Conductivity |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | -
19 |  | Vacuum Possibility |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | -
20 |  | Bi-Directional Flow
21
22 | METER | Process Connection |  | Size |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | *
23 |  |  |  | Rating (ANSI) |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF
24 |  | Electrode Type |  |  |  | MFR. STD |  |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  |  | MFR. STD |  |  |  | MFR. STD
25 |  | Accuracy |  |  |  | ± 0.5% of Full Scale |  |  |  |  | ± 0.5% of Full Scale |  |  |  | ± 0.5% of Full Scale |  |  |  | ± 0.5% of Full Scale |  |  |  | ± 0.5% of Full Scale |  |  |  |  | ± 0.5% of Full Scale |  |  |  | ± 0.5% of Full Scale
26 |  | Calibrated Flow Range |  |  |  | 0 ~ 80 |  |  |  |  | 0 ~ 55 |  |  |  | 0 ~ 2 |  |  |  | 0 ~ 50 |  |  |  | 0 ~ 25 |  |  |  |  | 0 ~ 50 |  |  |  | 0 ~ 25
27 |  |  |  | Body, Flange |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS
28 |  | Material |  | Liner |  | PFA |  |  |  |  | PFA |  |  |  | PFA |  |  |  | PFA |  |  |  | PFA |  |  |  |  | PFA |  |  |  | PFA
29 |  |  |  | Electrode |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS
30 |  |  |  | Grounding |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  |  | 316LSS |  |  |  | 316LSS
31 |  | Grounding Type |  |  |  | GROUND RING |  |  |  |  | GROUND RING |  |  |  | GROUND RING |  |  |  | GROUND RING |  |  |  | GROUND RING |  |  |  |  | GROUND RING |  |  |  | GROUND RING
32
33
34 | TRANSMITTER | Scale Range |  |  |  | 0 ~ 80 |  |  |  |  | 0 ~ 55 |  |  |  | 0 ~ 2 |  |  |  | 0 ~ 50 |  |  |  | 0 ~ 25 |  |  |  |  | 0 ~ 50 |  |  |  | 0 ~ 25
35 |  | Output Signal |  |  |  | 4~20mA HART |  |  |  |  | 4~20mA HART |  |  |  | 4~20mA HART |  |  |  | 4~20mA HART |  |  |  | 4~20mA HART |  |  |  |  | 4~20mA HART |  |  |  | 4~20mA HART
36 |  | Power Supply |  |  |  | AC 110V, 60Hz |  |  |  |  | AC 110V, 60Hz |  |  |  | AC 110V, 60Hz |  |  |  | AC 110V, 60Hz |  |  |  | AC 110V, 60Hz |  |  |  |  | AC 110V, 60Hz |  |  |  | AC 110V, 60Hz
37 |  | Electrical Connection |  |  |  | 1/2" NPT x 2ea |  |  |  |  | 1/2" NPT x 2ea |  |  |  | 1/2" NPT x 2ea |  |  |  | 1/2" NPT x 2ea |  |  |  | 1/2" NPT x 2ea |  |  |  |  | 1/2" NPT x 2ea |  |  |  | 1/2" NPT x 2ea
38 |  | Mounting Type |  |  |  | INTEGRAL |  |  |  |  | INTEGRAL |  |  |  | INTEGRAL |  |  |  | INTEGRAL |  |  |  | INTEGRAL |  |  |  |  | INTEGRAL |  |  |  | INTEGRAL
39
40 | OPTION | Special Cable
41 |  | Mounting Bracket
42 |  | Cable Gland
43
44 | PROQ. | Manufacturer
45 |  | Model
46
47
[7 empty] | NOTE | [16 empty] | NOTE
[7 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor.
[7 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied.