## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | ROTAMETER | [5 empty] | DS-IN-F-007
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
ROTAMETER
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | MAY.24.'18 |  |  | FOR QUOTAION |  | J.H Jung |  | C.M Lee | K.Y Noh |  |  | H.D Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-007 |  |  | 2018.05.24

## Rotameter
[5 empty] | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT
[17 empty] | LG Chem | [15 empty] | LG Chem
[17 empty] | DOC. NO. | [15 empty] | DOC. NO.
| JOB NO. |  | : M0556 |  | ROTAMETER | [11 empty] | DS-IN-F-007 |  |  |  | ROTAMETER | [11 empty] | DS-IN-F-007
| PROJECT NAME |  | : IPA 50KTA Exp. | [13 empty] | REV. NO. | [15 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [13 empty] | A | [15 empty] | A
1 | GENERAL | Tag No. |  |  | FI-1374 |  |  |  | FI-1390 |  |  |  | FI-1860 |  |  |  | FI-1861 |  |  |  | FT-1112 |  |  |  | FT-1356-1 |  |  |  | FT-1360
2 |  | P&ID No. |  |  | D-1-IPA-3007 |  |  |  | D-1-IPA-3007 |  |  |  | D-1-IPA-8023 |  |  |  | B-1-9133 |  |  |  | D-1-IPA-1001 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3005
3 |  | Service |  |  | GA-374A/B DISCHARGE |  |  |  | NL TO BI-510 |  |  |  | - |  |  |  | - |  |  |  | WT TO GA-110A/B |  |  |  | GA-356A/B DISCH. TO FA-374 |  |  |  | PW TO EA-355 OUTLET
4 |  | Line Class |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  | BB55C1
5 |  | Line Size |  | Line Schedule | 2" |  |  |  | 3/4" |  |  |  | 1" |  |  |  | 1 1/2" |  |  |  | 1" |  |  |  | 1" |  |  |  | 1"
6 |  | Nace Requirement
7 |  | Enclosure Class | [18 empty] | Ex d IIB T4, IP 56 |  |  |  | Ex d IIB T4, IP 56 |  |  |  | Ex d IIB T4, IP 56
8
9 | SERVICE CONDITION | Fluid |  |  | PDI |  |  |  | NL |  |  |  | NL |  |  |  | NL |  |  |  | WT |  |  |  | PDI |  |  |  | PW
10 |  | Flow Rate Unit |  | State | m3/h |  |  | L | Nm3/h |  |  | V | kg/h |  |  | V | kg/h |  |  | V | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L
11 |  |  |  |  | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN
12 |  | Flow Rate |  |  | 6.1545 | 5.1288 |  | - | 24 | - |  | - | - | - |  | - | - | - |  | - | HOLD | HOLD |  | - | 1.86 | 1.55 |  | - | HOLD | HOLD |  | -
13 |  | Inlet Pressure |  | (kg/cm2g) | - | 2.35 |  | - | - | 6 |  | - | - | - |  | - | - | - |  | - | - | - |  | - | - | 3.44 |  | - | - | 5 |  | -
14 |  | Temperature |  | (deg C) | - | 70 |  | - | - | AMB |  | - | - | - |  | - | - | - |  | - | - | AMB |  | - | - | 40.3 |  | - | - | AMB |  | -
15 |  | S.G. @ Op |  | Density @ Op |  |  | 800 |  |  |  | 7.814 |  |  |  | - |  |  |  | - |  |  |  | 998.5 |  |  |  | 906.48 |  |  |  | 997.4
16 |  | Viscosity @ Op. |  | Molcular Mass | 1 |  | - |  | 0.0178 |  | 28 |  | - |  | - |  | - |  | - |  | 1.0014 |  | - |  | 0.7083 |  | - |  | 0.89 |  | -
17 |  | Specific Heat Ratio |  | Comp. Factor (Z) | - |  | - |  | 1.411 |  | 0.99746 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
18 |  | Max. Allowable Pressure Drop |  |  | 0.2 |  |  |  | 0.2 |  |  |  | 0.2 |  |  |  | 0.2 |  |  |  | 0.2 |  |  |  | 0.2 |  |  |  | 0.2
19 |  | Design Pressure |  | (kg/cm2g) | 3.2 |  |  |  | 10 |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | 5.7 |  |  |  | 7
20 |  | Design Temperature |  | (deg C) | 150 |  |  |  | 60 |  |  |  | - |  |  |  | - |  |  |  | AMB |  |  |  | 120 |  |  |  | AMB
21
22 | METER | Connection Size & Rating |  |  | 2" 150# RF |  |  |  | 3/4" 150# RF |  |  |  | 1" 150# RF |  |  |  | 1 1/2" 150# RF |  |  |  | 1" 150# RF |  |  |  | 1" 150# RF |  |  |  | 1" 150# RF
23 |  | Inlet / Outlet Direction |  |  | BOTTOM-TOP |  |  |  | BOTTOM-TOP |  |  |  | BOTTOM-TOP |  |  |  | BOTTOM-TOP |  |  |  | BOTTOM-TOP |  |  |  | BOTTOM-TOP |  |  |  | BOTTOM-TOP
24 |  | Float Guide Type |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
25 |  | Calibrated Flow Range |  |  | 1 ~ 10 |  |  |  | 3 ~ 30 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 0.2 ~ 2 |  |  |  | 0.02 ~ 0.2
26 |  |  | Fitting |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
27 |  | Material | Packing or O-Ring |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
28 |  |  | Tube |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316LSS |  |  |  | 316SS |  |  |  | 316SS
29 |  |  | Float |  | 304SS |  |  |  | 304SS |  |  |  | 304SS |  |  |  | 304SS |  |  |  | 316LSS |  |  |  | 304SS |  |  |  | 304SS
30 |  |  | Diaphragm of Regulator |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | -
31 |  | Rated Accuracy |  |  | ± 2% OF F.S |  |  |  | ± 2% OF F.S |  |  |  | ± 2% OF F.S |  |  |  | ± 2% OF F.S |  |  |  | ± 2% OF F.S |  |  |  | ± 2% OF F.S |  |  |  | ± 2% OF F.S
32 |  | Hydrauric Calibration Required
33
34 | TRANSMITTER | Scale Range | [18 empty] | HOLD |  |  |  | 0.2 ~ 2 |  |  |  | HOLD
35 |  | Output Signal | [18 empty] | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART
36 |  | Electrical Connection | [18 empty] | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT
37
38
39 | SWITCH | Quantity
40 |  | Form
41 |  | Rating
42
43
44 | ACCESSORIES | Valve Size |  | Location | 2" |  | OUTLET |  | 3/4" |  | OUTLET |  | 1" |  | OUTLET |  | 1 1/2" |  | OUTLET |  | 1" |  | OUTLET |  | 1" |  | OUTLET |  | 1" |  | OUTLET
45 |  | Valve Material |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316LSS |  |  |  | 316SS |  |  |  | 316SS
46 |  | Purge Meter Tubing
47 |  | Air Set
48 |  | Damper |  |  | - |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | - |  |  |  | - |  |  |  | -
49 |  | Cooling Fin
50 |  | Cable Gland
51 |  | Constant Flow |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | -
52 | PROQ. | Manufacturer
53 |  | Model
54
55
NOTE