## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | RADAR LEVEL INSTRUMENT | [5 empty] | DS-IN-F-011
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | B
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
RADAR LEVEL INSTRUMENT
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
B |  | AUG.06.'18 |  |  | FOR QUOTAION |  | J.H.Jung |  | C.M Lee | K.Y Noh |  |  | H.D.Yoon
A |  | JUL.17.'18 |  |  | FOR QUOTAION |  | J.H.Jung |  | C.M Lee | K.Y Noh |  |  | H.D.Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-011 |  |  | 2018.08.06

## RADAR
[5 empty] | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [10 empty] | CLIENT |  |  | DATA SHEET | [9 empty] | CLIENT
[17 empty] | LG Chem | [14 empty] | LG Chem | [12 empty] | LG Chem
[17 empty] | DOC. NO. | [14 empty] | DOC. NO. | [12 empty] | DOC. NO.
| JOB NO. |  | : M0556 |  | RADAR LEVEL INSTRUMENT | [11 empty] | DS-IN-F-011 |  |  |  | RADAR LEVEL INSTRUMENT | [10 empty] | DS-IN-F-011 |  |  | RADAR LEVEL INSTRUMENT | [9 empty] | DS-IN-F-011
| PROJECT NAME |  | : IPA 50KTA Exp. | [13 empty] | REV. NO. | [14 empty] | REV. NO. | [12 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [13 empty] | B | [14 empty] | B | [12 empty] | B
1 | GENERAL | Tag No. |  |  | LT-1420A |  |  |  | LT-1420B |  |  |  | LT-1421A |  |  |  | LT-1421B |  |  |  | LT-1820 |  |  |  | LT-1840 | [9 empty] | LT-1375 | [12 empty] | 7
2 |  | P&ID No. |  |  | D-1-IPA-4002 |  |  |  | D-1-IPA-4002 |  |  |  | D-1-IPA-4002 |  |  |  | D-1-IPA-4002 |  |  |  | D-1-IPA-8012 |  |  |  | D-1-IPA-8024 | [9 empty] | D-1-IPA-3007
3 |  | Service |  |  | FB-420A |  |  |  | FB-420B |  |  |  | FB-420A |  |  |  | FB-420B |  |  |  | EF-820 |  |  |  | OILY WATER POND | [9 empty] | FA-374
4 |  | Equipment No. |  | Equipment Type | FB-420A |  | TANK |  | FB-420B |  | TANK |  | FB-420A |  | TANK |  | FB-420B |  | TANK |  | EF-820 |  | BASIN |  | - |  | PIT | [7 empty] | FA-374 |  | VESSEL
5 |  | Equipment Size
6 |  | Nace Requirement
7 |  | Enclosure Class |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 | [9 empty] | Ex d IIB T4, IP56
8
9 | SERVICE CONDITION | Upper Fluid |  | State
10 |  | Lower Fluid |  | State | IPA |  |  | L | IPA |  |  | L | IPA |  |  | L | IPA |  |  | L | RAW WATER |  |  | L | DILUTE IPA |  |  | L | [6 empty] | DILUTE IPA |  |  | L
11 |  |  |  |  | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX | NOR | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX | NOR | MIN | MAX | NOR | MIN
12 |  | Pressure |  | (kg/cm2g) |  | ATM |  |  |  | ATM |  |  |  | ATM |  |  |  | ATM |  |  |  | 4 |  |  |  | 0 | [9 empty] | ATM
13 |  | Temperature |  | (deg C) |  | AMB |  |  |  | AMB |  |  |  | AMB |  |  |  | AMB |  |  |  | AMB |  |  |  | AMB | [9 empty] | 70
14 |  | Upper Fluid S.G. @ Op
15 |  | Lower Fluid S.G. @ Op |  |  | 774.8 |  |  |  | 774.8 |  |  |  | 774.8 |  |  |  | 774.8 |  |  |  | 998.39 |  |  |  | 998 | [9 empty] | 800
16
17
18 | BODY | Connection Size |  | Rating | 3" |  | 150# RF |  | 3" |  | 150# RF |  | 3" |  | 150# RF |  | 3" |  | 150# RF |  | 3" |  | 150# RF |  | 3" |  | 150# RF | [7 empty] | 3" |  | 150# RF
19 |  | SensorType |  |  | NON CONTACT TYPE |  |  |  | NON CONTACT TYPE |  |  |  | NON CONTACT TYPE |  |  |  | NON CONTACT TYPE |  |  |  | NON CONTACT TYPE |  |  |  | NON CONTACT TYPE | [9 empty] | GWR (ROD TYPE)
20 |  | Maeasuring Range |  |  | 15500mm |  |  |  | 15500mm |  |  |  | 15500mm |  |  |  | 15500mm |  |  |  | HOLD |  |  |  | HOLD | [9 empty] | 2150mm
21 |  | Frequency |  |  | MFR.STD |  |  |  | MFR.STD |  |  |  | MFR.STD |  |  |  | MFR.STD |  |  |  | MFR.STD |  |  |  | MFR.STD | [9 empty] | MFR.STD
22 |  |  |  | Flange | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS | [9 empty] | 316SS
23 |  | Material |  | Wetted Parts | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS | [9 empty] | 316LSS
24 |  |  |  | Chamber | [30 empty] | 304SS
25
26
27 | TRANSMITTER | Mounting |  |  | INTERNAL |  |  |  | INTERNAL |  |  |  | INTERNAL |  |  |  | INTERNAL |  |  |  | INTERNAL |  |  |  | INTERNAL | [9 empty] | INTERNAL
28 |  | Output Signal |  |  | 4-20mA DC w/HART |  |  |  | 4-20mA DC w/HART |  |  |  | 4-20mA DC w/HART |  |  |  | 4-20mA DC w/HART |  |  |  | 4-20mA DC w/HART |  |  |  | 4-20mA DC w/HART | [9 empty] | 4-20mA DC w/HART
29 |  | Power Supply |  |  | DC 24V (Loop Power) |  |  |  | DC 24V (Loop Power) |  |  |  | DC 24V (Loop Power) |  |  |  | DC 24V (Loop Power) |  |  |  | DC 24V (Loop Power) |  |  |  | DC 24V (Loop Power) | [9 empty] | DC 24V (Loop Power)
30 |  | Electrical Connection |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT | [9 empty] | 1/2" NPT
31 |  | Accuracy |  |  | ± 0.5% of F.S |  |  |  | ± 0.5% of F.S |  |  |  | ± 0.5% of F.S |  |  |  | ± 0.5% of F.S |  |  |  | ± 0.5% of F.S |  |  |  | ± 0.5% of F.S | [9 empty] | ± 0.5% of F.S
25 |  | Painting (Color) |  |  | MFR.STD |  |  |  | MFR.STD |  |  |  | MFR.STD |  |  |  | MFR.STD |  |  |  | MFR.STD |  |  |  | MFR.STD | [9 empty] | MFR.STD
32
33 | ACCESSORIES | Local Remote Indicator
34 |  | Self Test
35 |  | Special Cable
36 |  | Cable Gland
37 |  | Air Purge
38
39 | PROQ. | Manufacturer
40 |  | Model
41
[5 empty] | NOTE | [15 empty] | NOTE | [13 empty] | NOTE