## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | LEVEL GAUGE | [5 empty] | DS-IN-F-015
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | B
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
LEVEL GAUGE
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
B |  | AUG.07.'18 |  |  | FOR QUOTAION |  | J.H.Jung |  | C.M Lee | K.Y Noh |  |  | H.D.Yoon
A |  | JUL.17.'18 |  |  | FOR QUOTAION |  | J.H.Jung |  | C.M Lee | K.Y Noh |  |  | H.D.Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-015 |  |  | 2018.08.07

## Level Gauge
[5 empty] | DATA SHEET | [6 empty] | CLIENT |  | DATA SHEET | [7 empty] | CLIENT |  | DATA SHEET | [6 empty] | CLIENT |  | DATA SHEET | [7 empty] | CLIENT |  | DATA SHEET | [6 empty] | CLIENT |  | DATA SHEET | [6 empty] | CLIENT |  | DATA SHEET | [6 empty] | CLIENT |  | DATA SHEET | [6 empty] | CLIENT |  | DATA SHEET | [7 empty] | CLIENT
[12 empty] | LG Chem | [9 empty] | LG Chem | [8 empty] | LG Chem | [9 empty] | LG Chem | [8 empty] | LG Chem | [8 empty] | LG Chem | [8 empty] | LG Chem | [8 empty] | LG Chem | [9 empty] | LG Chem
[12 empty] | DOC. NO. | [9 empty] | DOC. NO. | [8 empty] | DOC. NO. | [9 empty] | DOC. NO. | [8 empty] | DOC. NO. | [8 empty] | DOC. NO. | [8 empty] | DOC. NO. | [8 empty] | DOC. NO. | [9 empty] | DOC. NO.
| JOB NO. |  | : M0556 |  | LEVEL GAUGE | [6 empty] | DS-IN-F-015 |  | LEVEL GAUGE | [7 empty] | DS-IN-F-015 |  | LEVEL GAUGE | [6 empty] | DS-IN-F-015 |  | LEVEL GAUGE | [7 empty] | DS-IN-F-015 |  | LEVEL GAUGE | [6 empty] | DS-IN-F-015 |  | LEVEL GAUGE | [6 empty] | DS-IN-F-015 |  | LEVEL GAUGE | [6 empty] | DS-IN-F-015 |  | LEVEL GAUGE | [6 empty] | DS-IN-F-015 |  | LEVEL GAUGE | [7 empty] | DS-IN-F-015
| PROJECT NAME |  | : IPA 50KTA Exp. | [8 empty] | REV. NO. | [9 empty] | REV. NO. | [8 empty] | REV. NO. | [9 empty] | REV. NO. | [8 empty] | REV. NO. | [8 empty] | REV. NO. | [8 empty] | REV. NO. | [8 empty] | REV. NO. | [9 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [8 empty] | B | [9 empty] | B | [8 empty] | B | [9 empty] | B | [8 empty] | B | [8 empty] | B | [8 empty] | B | [8 empty] | B | [9 empty] | B
1 | GENERAL | Tag No. |  |  | LG-1110 |  |  | LG-1113 |  | LG-1151 |  | LG-1157A/B |  | LG-1158A/B |  |  |  | LG-1162 |  | LG-1170-1 |  | LG-1211 |  | LG-1212 |  |  | LG-1221 |  | LG-1226 |  | LG-1227 |  | LG-1311 |  |  |  | LG-1315 |  | LG-1316 |  | LG-1317 |  | LG-1321 |  |  | LG-1326 |  | LG-1331 |  | LG-1352 |  | LG-1355 |  |  | LG-1356 |  | LG-1361 |  | LG-1366 |  | LG-1372A/B/C |  |  | LG-1374AA/AB/AC |  | LG-1374BA/BB/BC |  | LG-1374CA/CB/CC |  | LG-1415 |  |  | LG-1781A/B/C |  | LG-1782A/B/C |  | LG-1813 |  | LG-1816 |  |  |  | LG-1830 |  | LG-1831 |  | LG-1860 |  | 36
2 |  | Quantity |  |  | 1 |  |  | 1 |  | 1 |  | 2 |  | 2 |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  |  | 1 |  | 1 |  | 1 |  | 1 |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  |  | 1 |  | 1 |  | 1 |  | 1 |  |  | 1 |  | 1 |  | 1 |  | 3 |  |  | 3 |  | 3 |  | 3 |  | 1 |  |  | 3 |  | 3 |  | 1 |  | 1 |  |  |  | 1 |  | 1 |  | 1 |  | 50
3 |  | P&ID No. |  |  | D-1-IPA-1001 |  |  | D-1-IPA-1001 |  | D-1-IPA-1002 |  | D-1-IPA-1003 |  | D-1-IPA-1003 |  |  |  | D-1-IPA-1003 |  | D-1-IPA-1003 |  | D-1-IPA-2001 |  | D-1-IPA-2001 |  |  | D-1-IPA-2002 |  | D-1-IPA-2002 |  | D-1-IPA-2002 |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3001 |  | D-1-IPA-3001 |  | D-1-IPA-3001 |  | D-1-IPA-3002 |  |  | D-1-IPA-3003 |  | D-1-IPA-3002 |  | D-1-IPA-3004 |  | D-1-IPA-3004 |  |  | D-1-IPA-3004 |  | D-1-IPA-3006 |  | D-1-IPA-3006 |  | D-1-IPA-3007 |  |  | D-1-IPA-3007 |  | D-1-IPA-3007 |  | D-1-IPA-3007 |  | D-1-IPA-4001 |  |  | D-1-IPA-7001 |  | D-1-IPA-7001 |  | D-1-IPA-8011 |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8013 |  | D-1-IPA-8013 |  | D-1-IPA-8023
4 |  | Service |  |  | FA-110 |  |  | FA-112 |  | DA-140 |  | FC-150 |  | FC-155 |  |  |  | FC-160 |  | FC-170 |  | DA-210 |  | FA-215 |  |  | DA-220 |  | FA-225 |  | FA-223 |  | DA-310 |  |  |  | FC-315 |  | FC-315 |  | HC TO FC-315 |  | DA-320 |  |  | FA-325 |  | DA-330 |  | DA-350 |  | FC-355 |  |  | FC-355 |  | DA-360 |  | FA-365 |  | FA-371 |  |  | FA-373A |  | FA-373B |  | FA-373C |  | FA-415 |  |  | FA-781A |  | FA-781B |  | FC-812 |  | FA-815 |  |  |  | FA-830X |  | EA-830X |  | FA-860
5 |  | Vessel No. |  |  | FA-110 |  |  | FA-112 |  | DA-140 |  | FC-150 |  | FC-155 |  |  |  | FC-160 |  | FC-170 |  | DA-210 |  | FA-215 |  |  | DA-220 |  | FA-225 |  | FA-223 |  | DA-310 |  |  |  | FC-315 |  | FC-315 |  | - |  | DA-320 |  |  | FA-325 |  | DA-330 |  | DA-350 |  | FC-355 |  |  | FC-355 |  | DA-360 |  | FA-365 |  | FA-371 |  |  | FA-373A |  | FA-373B |  | FA-373C |  | FA-415 |  |  | FA-781A |  | FA-781B |  | FC-812 |  | FA-815 |  |  |  | FA-830X |  | EA-830X |  | FA-860
6 |  | Nace Requirement
7 |  | Enclosure Class
8
9 | SERVICE CONDITION | Upper Fluid
10 |  | Lower Fluid |  |  | H3PO4 |  |  | CAUSTIC 20 wt% |  | DILUTE IPA |  | DILUTE IPA |  | DILUTE IPA |  |  |  | DILUTE IPA |  | PRG |  | PHE |  | PROPYLENE |  |  | PHE |  | PROPYLENE |  | PHE |  | DILUTE IPA |  |  |  | WATER |  | HC |  | HC |  | WASH WATER |  |  | DILUTE IPA |  | DILUTE IPA |  | IPA |  | SOLVENT |  |  | DILUTE IPA |  | PROCESS WATER |  | DILUTE IPA |  | DILUTE IPA |  |  | IPA |  | IPA |  | IPA |  | PROPYLENE |  |  | DILUTE IPA |  | DILUTE IPA |  | CONDENSATE |  | CONDENSATE |  |  |  | POLISHED WATER |  | POLISHED WATER |  | DILUTE IPA
11 |  | Pressure @ Max |  | @ Nor (kg/cm2g) |  |  | ATM |  | ATM |  | 31.6 |  | 16.8 |  |  |  | 0.2 |  | 0.2 |  | HOLD |  | 16.53 |  |  | 16.4 |  | 19.6 |  | 19 |  | 5.5 |  |  |  | 0.25 |  | 0 |  | 0 |  | 0 |  |  | 2 |  | 0.02 |  | 2.1 |  | 0.35 |  |  | 0 |  | 0 |  | 0.33 |  | 0 |  |  | 0.03 / -0.02 |  | 0.03 / -0.02 |  | 0.03 / -0.02 |  | 0.03 / -0.02 |  |  | 15.2 |  | ATM |  | ATM |  | 3.5 |  |  |  | ATM |  | 0.25 |  | 0.75 |  | 0.3
12 |  | Temperature @ Max |  | @ Nor (deg C) |  |  | 20 |  | 20 |  | 94 |  | 93 |  |  |  | 82 |  | 77.9 |  | HOLD |  | 175.3 |  |  | 40 |  | 52.4 |  | 47 |  | 30 |  |  |  | 97 |  | 45 |  | 45 |  | 45 |  |  | 133.3 |  | 50 |  | 117.3 |  | 89.6 |  |  | 40 |  | 40 |  | 108 |  | 74 |  |  | 50 |  | 50 |  | 50 |  | 50 |  |  | AMB |  | AMB |  | AMB |  | 147 |  |  |  | 100 |  | 105 |  | 106.8 |  | AMB
13 |  | S.G Upper |  | Lower |  |  | 1.21 |  | 0.122 |  | 0.856 |  | 0.849 |  |  |  | 0.881 |  | 0.739 |  | HOLD |  | 0.486 |  |  | 0.454 |  | 0.443 |  | 0.47 |  | 0.44 |  |  |  | 0.902 |  | 0.969 |  | 0.682 |  | 0.826 |  |  | 0.882 |  | 0.787 |  | 0.758 |  | 0.712 |  |  | 0.802 |  | 0.907 |  | 0.91 |  | 0.765 |  |  | 0.79 |  | 0.78 |  | 0.78 |  | 0.78 |  |  | 0.51 |  | 0.689 |  | 0.877 |  | 0.92 |  |  |  | 0.96 |  | 0.954 |  | 0.954 |  | 0.84
14 |  | Viscosity Upper |  | Lower (cP) |  |  | 4 |  | 5 |  | 0.28898 |  | 0.25004 |  |  |  | 0.25004 |  | 0.38061 |  | HOLD |  | 0.116 |  |  | 0.065 |  | 0.073 |  | 0.056 |  | 0.119 |  |  |  | 0.293 |  | 0.611 |  | 0.24 |  | 0.611 |  |  | 0.2 |  | 0.848 |  | 0.229 |  | 0.419 |  |  | 0.73 |  | 0.71 |  | 0.257 |  | 0.456 |  |  | 1.34 |  | 0.7273 |  | 0.7273 |  | 0.7273 |  |  | 0.08 |  | 0.258 |  | 0.771 |  | 0.186 |  |  |  | 0.279 |  | 0.26 |  | 0.26 |  | 0.5
15 |  | Design Pressure |  | (kg/cm2g) |  |  | 0.5 |  | 0.5 |  | 55 |  | 20 |  |  |  | 2 |  | 2 |  | HOLD |  | 25 |  |  | 25 |  | 25 |  | 25 |  | 7.5 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  |  | 4 |  | 2 |  | 4 |  | 2 |  |  | 2 |  | 2 |  | 2 |  | 2 |  |  | 0.5 / -0.1 |  | 0.5 / -0.1 |  | 0.5 / -0.1 |  | 0.5 / -0.1 |  |  | 25 |  | 0.5 / -0.1 |  | 0.5 / -0.1 |  | 6 |  |  |  | 2 |  | 4.0 / F.V |  | 9.24 / F.V |  | 2
16 |  | Design Temperature |  | (deg C) |  |  | 120 |  | 120 |  | 150 |  | 140 |  |  |  | 120 |  | 120 |  | HOLD |  | 200 |  |  | 120 |  | 120 |  | 120 |  | 120 |  |  |  | 150 |  | 120 |  | 120 |  | 120 |  |  | 180 |  | 140 |  | 160 |  | 120 |  |  | 120 |  | 120 |  | 140 |  | 120 |  |  | 120 |  | 120 |  | 120 |  | 120 |  |  | 65 / -15 |  | 120 |  | 120 |  | 200 |  |  |  | 150 |  | 180 |  | 180 |  | 300
17
18
19 | GAUGE | Type |  |  | MAGNETIC |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC |  |  |  | MAGNETIC |  | MAGNETIC |  | MAGNETIC
20 |  | Visible Length |  | C to C |  |  | 1220 |  | 1540 |  | 2400 |  | 2970 |  |  |  | 2970 |  | 700 |  | NOTE 1 |  | 1300 |  |  | 1140 |  | 1300 |  | 1380 |  | 900 |  |  |  | 3100 |  | 800 |  | 800 |  | NOTE 1 |  |  | 3100 |  | 1700 |  | 1600 |  | 1500 |  |  | 2600 |  | 2600 |  | 1300 |  | 1220 |  |  | 3000 |  | 3000 |  | 3000 |  | 3000 |  |  | 2100 |  | 2700 |  | 2700 |  | 2800 |  |  |  | 2080 |  | NOTE 1 |  | NOTE 1 |  | 1500
21 |  | Connection Size |  | Rating | 1" |  | 150# RF | 1" | 150# RF | 1" | 600# RF | 1" | 300# RF | 1" |  |  | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" | 300# RF | 1" |  | 300# RF | 1" | 300# RF | 1" | 300# RF | 1" | 150# RF | 1" |  |  | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" |  | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" |  | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" |  | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" |  | 300# RF | 1" | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" |  |  | 150# RF | 1" | 150# RF | 1" | 150# RF | 1" | 150# RF
22 |  | Connection Arrangement
23 |  | Body Material |  |  | 316LSS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  |  | 304SS |  | 304SS |  | 304SS
24 |  | Gasket Material |  |  | MFR STD |  |  | MFR STD |  | MFR STD |  | MFR STD |  | MFR STD |  |  |  | MFR STD |  | MFR STD |  | MFR STD |  | MFR STD |  |  | MFR STD |  | MFR STD |  | MFR STD |  | MFR STD |  |  |  | MFR STD |  | MFR STD |  | MFR STD |  | MFR STD |  |  | MFR STD |  | MFR STD |  | MFR STD |  | MFR STD |  |  | MFR STD |  | MFR STD |  | MFR STD |  | MFR STD |  |  | MFR STD |  | MFR STD |  | MFR STD |  | MFR STD |  |  | MFR STD |  | MFR STD |  | MFR STD |  | MFR STD |  |  |  | MFR STD |  | MFR STD |  | MFR STD
25 |  | Float Material |  |  | TITANUM |  |  | TITANUM |  | TITANUM |  | TITANUM |  | TITANUM |  |  |  | TITANUM |  | TITANUM |  | TITANUM |  | TITANUM |  |  | TITANUM |  | TITANUM |  | TITANUM |  | TITANUM |  |  |  | TITANUM |  | TITANUM |  | TITANUM |  | TITANUM |  |  | TITANUM |  | TITANUM |  | TITANUM |  | TITANUM |  |  | TITANUM |  | TITANUM |  | TITANUM |  | TITANUM |  |  | TITANUM |  | TITANUM |  | TITANUM |  | TITANUM |  |  | TITANUM |  | TITANUM |  | TITANUM |  | TITANUM |  |  |  | TITANUM |  | TITANUM |  | TITANUM
26 |  | Mica Shield
27 |  | Illuminator |  | Power Supply
28 |  | Jacket or Internal Tracer
29 |  | Frost Extension |  | Length
30 |  | Calibration Scale |  |  | YES |  |  | YES |  | YES |  | YES |  | YES |  |  |  | YES |  | YES |  | YES |  | YES |  |  | YES |  | YES |  | YES |  | YES |  |  |  | YES |  | YES |  | YES |  | YES |  |  | YES |  | YES |  | YES |  | YES |  |  | YES |  | YES |  | YES |  | YES |  |  | YES |  | YES |  | YES |  | YES |  |  | YES |  | YES |  | YES |  | YES |  |  |  | YES |  | YES |  | YES
31 |  | Glass Size
32
33
34 | VALVE | Type
35 |  | Bonnet Type
36 |  | Body Material
37 |  | Trim Material
38 |  | Packing Material
39 |  | Ball Check
40 |  | Vessel Conn. Size |  | Rating
41 |  | Gauge Conn. Size |  | Rating
42 |  | Gauge Conn. Union
43 |  | Renewable Seat
44
45
46 | OPTION | Drain Part |  |  | DRAIN VALVE W/PLUG |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  |  |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG |  | DRAIN VALVE W/PLUG
47 |  | Drain Part Connection Size |  |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT
48 |  | Drain Valve Material |  |  | 316LSS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  | 304SS |  | 304SS |  | 304SS |  | 304SS |  |  |  | 304SS |  | 304SS |  | 304SS
49 |  | Vent Part |  |  | PLUG |  |  | PLUG |  | PLUG |  | PLUG |  | PLUG |  |  |  | PLUG |  | PLUG |  | PLUG |  | PLUG |  |  | PLUG |  | PLUG |  | PLUG |  | PLUG |  |  |  | PLUG |  | PLUG |  | PLUG |  | PLUG |  |  | PLUG |  | PLUG |  | PLUG |  | PLUG |  |  | PLUG |  | PLUG |  | PLUG |  | PLUG |  |  | PLUG |  | PLUG |  | PLUG |  | PLUG |  |  | PLUG |  | PLUG |  | PLUG |  | PLUG |  |  |  | PLUG |  | PLUG |  | PLUG
50 |  | Vent Part Connection Size |  |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT |  |  |  | 1/2" NPT |  | 1/2" NPT |  | 1/2" NPT
51 |  | Vent Valve Material
52 |  | Center Support Clip
53
54 | PROQ. | Manufacturer
55 |  | Model
56
[6 empty] | NOTE | [8 empty] | NOTE | [9 empty] | NOTE | [8 empty] | NOTE | [9 empty] | NOTE | [8 empty] | NOTE | [8 empty] | NOTE | [8 empty] | NOTE | [8 empty] | NOTE
[15 empty] | 1. | Vendor shall assume C-C length as 2500 mm | [17 empty] | 1. | Vendor shall assume C-C length as 2500 mm | [44 empty] | 1. | Vendor shall assume C-C length as 2500 mm