## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | FIELD TRANSMITTER (FLOW) | [5 empty] | DS-IN-F-017A
| PROJECT NAME |  |  | : IPA Project | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA Project
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
FIELD TRANSMITTER
(FLOW)
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | JUL.16.'18 |  |  | FOR QUOTAION |  | J.H Jung |  | C.M Lee | K.Y Noh |  |  | H.D Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-017A |  |  | JUL.16.'18

## Flow
[5 empty] | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT
[17 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem
[17 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO.
| JOB NO. |  | : M0556 |  | FIELD TRANSMITTER (FLOW) | [11 empty] | DS-IN-F-017A |  |  |  | FIELD TRANSMITTER (FLOW) | [11 empty] | DS-IN-F-017A |  |  |  | FIELD TRANSMITTER (FLOW) | [11 empty] | DS-IN-F-017A |  |  |  | FIELD TRANSMITTER (FLOW) | [11 empty] | DS-IN-F-017A
| PROJECT NAME |  | : IPA Project | [13 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [13 empty] | A | [15 empty] | A | [15 empty] | A | [15 empty] | A
1 | GENERAL | Tag No. |  |  | FT-1119 |  |  |  | FT-1141 |  |  |  | FT-1142 |  |  |  | FT-1151 |  |  |  | FT-1165 |  |  |  | FT-1168 |  |  |  | FT-1311 |  |  |  | FT-1320 |  |  |  | FT-1321 |  |  |  | FT-1331 |  |  |  | FT-1335 |  |  |  | FT-1351 |  |  |  | FT-1352 |  |  |  | FT-1353 |  |  |  | FT-1801 |  |  |  | FT-1805
2 |  | P&ID No. |  |  | D-1-IPA-1001 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1003 |  |  |  | D-1-IPA-1003 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011
3 |  | Service |  |  | HP STEAM TO EA-110 |  |  |  | GB-120 DISCHARGE |  |  |  | GB-120 SUCTION |  |  |  | EA-140A/B WCS SUPPLY |  |  |  | EA-165 WCS SUPPLY |  |  |  | FC-170 FEED INLET |  |  |  | MP STEAM TO EA-311 |  |  |  | DA-320 FEED INLET |  |  |  | MP STEAM TO EA-321 |  |  |  | LP STEAM TO EA-331 |  |  |  | DA-330 OVHD TO DA-320 |  |  |  | DA-320 OVHD TO EA-351A/B |  |  |  | MP STEAM TO EA-352 |  |  |  | LP STEAM TO EA-352 |  |  |  | HS STEAM FROM B.L |  |  |  | MSS TO BG-803
4 |  | Line Class |  |  | BA59C |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  | BB57C |  |  |  | BB55C1 |  |  |  | BB57C |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB57C |  |  |  | BB55C |  |  |  | BA59C |  |  |  | BB57C
5 |  | Nace Requirement
6 |  | Enclosure Class |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56
7
8 | SERVICE CONDITION | Fluid |  |  | SH |  |  |  | PRG |  |  |  | PRG |  |  |  | WCS |  |  |  | WCS |  |  |  | PRG |  |  |  | SM |  |  |  | PDI |  |  |  | SM |  |  |  | SL |  |  |  | PDI |  |  |  | PDI |  |  |  | SM |  |  |  | SL |  |  |  | HS |  |  |  | MSS
9 |  | Flow Rate Unit |  | State | kg/h |  |  | S | kg/h |  |  | V | kg/h |  |  | V | m3/h |  |  | L | m3/h |  |  | L | kg/h |  |  | V | kg/h |  |  | S | m3/h |  |  | L | kg/h |  |  | S | kg/h |  |  | S | kg/h |  |  | V | kg/h |  |  | V | kg/h |  |  | S | kg/h |  |  | S | kg/h |  |  | S | kg/h |  |  | S
10 |  |  |  |  | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN
11 |  | Flow Rate |  |  | 7012 | 5843 |  |  | 223101.15 | 194001 |  |  | 223101 | 194001 |  |  | 313.4998 | 261.2499 |  |  | 62.1691 | 51.8076 |  |  | 1342.32 | 1118.6 |  |  | 3631.2 | 3026 |  |  | 132.0756 | 110.063 |  |  | 13024.8 | 10854 |  |  | 1806 | 1505 |  |  | 4252.5 | 3543.75 |  |  | 24554.04 | 20461.7 |  |  | 4800 | 587 |  |  | HOLD | HOLD |  |  | 26965 | 22160 |  |  | HOLD | HOLD
12 |  | Pressure |  | (kg/cm2g) |  | 31 |  |  |  | 47 |  |  |  | 31 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0.1 |  |  |  | 9.8 |  |  |  | 5.54 |  |  |  | 9.8 |  |  |  | 3.5 |  |  |  | 1.9 |  |  |  | 1.6 |  |  |  | 9.8 |  |  |  | 3.5 |  |  |  | 40 |  |  |  | 14.6
13 |  | Temperature |  | (deg C) |  | 255 |  |  |  | 125 |  |  |  | 94 |  |  |  | 32 |  |  |  | 32 |  |  |  | 38 |  |  |  | 198 |  |  |  | 97 |  |  |  | 198 |  |  |  | 147 |  |  |  | 111 |  |  |  | 106 |  |  |  | 198 |  |  |  | 147 |  |  |  | 340 |  |  |  | 226
14 |  | Design Pressure |  | (kg/cm2g) | 46 |  |  |  | 55 |  |  |  | 55 |  |  |  | 7 |  |  |  | 7 |  |  |  | 2 |  |  |  | 12 |  |  |  | 7.8 |  |  |  | 12 |  |  |  | 6 |  |  |  | 4 |  |  |  | 4 |  |  |  | 12 |  |  |  | 6 |  |  |  | 45 |  |  |  | HOLD
15 |  | Design Temperature |  | (deg C) | 400 |  |  |  | 180 |  |  |  | 150 |  |  |  | 50 |  |  |  | 50 |  |  |  | 120 |  |  |  | 250 |  |  |  | 150 |  |  |  | 250 |  |  |  | 200 |  |  |  | 180 |  |  |  | 180 |  |  |  | 250 |  |  |  | 200 |  |  |  | 425 |  |  |  | HOLD
16 |  | Density @ Op |  | (kg/m3) | 14.2 |  |  |  | 90 |  |  |  | 66.4 |  |  |  | 995.3 |  |  |  | 995.3 |  |  |  | 1.95 |  |  |  | 5.1 |  |  |  | 903.6 |  |  |  | 5.1 |  |  |  | 1.9 |  |  |  | 3.8 |  |  |  | 4 |  |  |  | 5.1 | [7 empty] | 15.5
17 |  | Viscosity @ Op. |  |  | 0.02 |  |  |  | 0.0143 |  |  |  | 0.01 |  |  |  | 0.76 |  |  |  | 0.76 |  |  |  | 0.01 |  |  |  | 0.02 |  |  |  | 0.29 |  |  |  | 0.02 |  |  |  | 0.01 |  |  |  | 0.01 |  |  |  | 0.01 |  |  |  | 0.02 | [7 empty] | 0.02
18
19 | TRANSMITTER | Application |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER |  |  |  | FLOW TRANSMITTER
20 |  | Mounting |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE
21 |  | Adjustable Range |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
22 |  | Set Range |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O |  |  |  | 2500 mmH2O
23 |  | Scale Range |  |  | 0 ~ 8500 |  |  |  | 0 ~ 270000 |  |  |  | 0 ~ 270000 |  |  |  | 0 ~ 400 |  |  |  | 0 ~ 80 |  |  |  | 0 ~ 1700 |  |  |  | 0 ~ 4500 |  |  |  | 0 ~ 160 |  |  |  | 0 ~ 16000 |  |  |  | 0 ~ 2200 |  |  |  | 0 ~ 5000 |  |  |  | 0 ~ 30000 |  |  |  | 0 ~ 5000 |  |  |  | - |  |  |  | 0 ~ 33000 |  |  |  | -
24 |  | Elevation / Suppression |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN |  |  |  | WITHIN MAX. SPAN
25 |  | Element Type |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM
26 |  | Element Material |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS
27 |  | Body Material |  | Body Rating | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD
28 |  | Process Flanges Material |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS
29 |  | Wetted O-Rings Material |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
30 |  | Output Signal |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART
31 |  | Housing Material |  | Painting | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD
32 |  | Power Supply |  | Accuracy | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2%
33 |  | High Side: Conn. Size & Rating |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT
34 |  | Low Side: Conn. Size & Rating |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT
35 |  | Electriccal Connection |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT
36
37 | DIAPHRAGM SEAL | Diaphragm Type |  | Extended Length |  |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH
38 |  | Diaphragm Material | [6 empty] | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS
39 |  | Fill Fluid | [6 empty] | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
40 |  | Capillary Material |  | Armor Material |  |  |  |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS
41 |  | Capillary Type |  | Capillary Length |  |  |  |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m
42 |  | Flush Ring | [6 empty] | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES
43
44 | ACCESSORIES | Display |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD
45 |  | Mounting Bracket |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE |  |  |  | 2" PIPE
46 |  | Hydrostatic Testing
47 |  | Valve Manifold Type |  |  | 3 WAY | [55 empty] | 3 WAY |  |  |  | 3 WAY
48 |  | Valve Manifold Material |  |  | 316SS | [55 empty] | 316SS |  |  |  | 316SS
49
50
51
52 | PROQ. | Manufacturer
53 |  | Model
54
NOTE