## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | FIELD TRANSMITTER (LEVEL) | [5 empty] | DS-IN-F-017B
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
FIELD TRANSMITTER
(LEVEL)
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | JUL.16.'18 |  |  | FOR QUOTAION |  | J.H.Jung |  | C.M Lee | K.Y Noh |  |  | H.D.Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-017B |  |  | JUL.16.'18

## LEVEL
[5 empty] | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [10 empty] | CLIENT |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [9 empty] | CLIENT |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT
[17 empty] | LG Chem | [15 empty] | LG Chem | [14 empty] | LG Chem | [14 empty] | LG Chem | [13 empty] | LG Chem | [14 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem
[17 empty] | DOC. NO. | [15 empty] | DOC. NO. | [14 empty] | DOC. NO. | [14 empty] | DOC. NO. | [13 empty] | DOC. NO. | [14 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO.
| JOB NO. |  | : M0556 |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [10 empty] | DS-IN-F-017B |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [9 empty] | DS-IN-F-017B |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B |  |  |  | FIELD TRANSMITTER (LEVEL) | [11 empty] | DS-IN-F-017B
| PROJECT NAME |  | : IPA 50KTA Exp. | [13 empty] | REV. NO. | [15 empty] | REV. NO. | [14 empty] | REV. NO. | [14 empty] | REV. NO. | [13 empty] | REV. NO. | [14 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [13 empty] | A | [15 empty] | A | [14 empty] | A | [14 empty] | A | [13 empty] | A | [14 empty] | A | [15 empty] | A | [15 empty] | A | [15 empty] | A | [15 empty] | A | [15 empty] | A | [15 empty] | A
1 | GENERAL | Tag No. |  |  | LT-1112 |  |  |  | LT-1113 |  |  |  | LT-1134 |  |  |  | LT-1141 |  |  |  | LT-1146A |  |  |  | LT-1147 |  |  |  | LT-1150 |  |  |  | LT-1157 |  |  |  | LT-1158 |  |  |  | LT-1161 | [9 empty] | LT-1210 |  |  |  | LT-1213 |  |  |  | LT-1220 |  |  |  | LT-1225 |  |  |  | LT-1228 | [12 empty] | LT-1310 |  |  |  | LT-1315 |  |  |  | LT-1316 |  |  |  | LT-1317 |  |  |  | LT-1320 |  |  |  | LT-1325 |  |  |  | LT-1330 |  |  |  | LT-1350 |  |  |  | LT-1351A |  |  |  | LT-1351B |  |  |  | LT-1354 |  |  |  | LT-1355 |  |  |  | LT-1356 |  |  |  | LT-1360 |  |  |  | LT-1366 |  |  |  | LT-1371 |  |  |  | LT-1373A |  |  |  | LT-1373B |  |  |  | LT-1373C |  |  |  | LT-1415 |  |  |  | LT-1781 |  |  |  | LT-1782 |  |  |  | LT-1812 |  |  |  | LT-1815 |  |  |  | LT-1830 |  |  |  | LT-1831 |  |  |  | LT-1860 |  |  |  | LT-1832 |  |  |  | 43
2 |  | P&ID No. |  |  | D-1-IPA-1001 |  |  |  | D-1-IPA-1001 |  |  |  | D-1-IPA-0004 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1003 |  |  |  | D-1-IPA-1003 |  |  |  | D-1-IPA-1003 | [9 empty] | D-1-IPA-2001 |  |  |  | D-1-IPA-2001 |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-2002 | [12 empty] | D-1-IPA-3001 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3006 |  |  |  | D-1-IPA-3006 |  |  |  | D-1-IPA-3007 |  |  |  | D-1-IPA-3007 |  |  |  | D-1-IPA-3007 |  |  |  | D-1-IPA-3007 |  |  |  | D-1-IPA-4001 |  |  |  | D-1-IPA-7001 |  |  |  | D-1-IPA-7001 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8013 |  |  |  | D-1-IPA-8013 |  |  |  | D-1-IPA-8023 |  |  |  | D-1-IPA-8013
3 |  | Service |  |  | EA-112 |  |  |  | FA-112 |  |  |  | FA-134 |  |  |  | FA-121 |  |  |  | FC-120 |  |  |  | FC-120 |  |  |  | DA-140 |  |  |  | FC-150 |  |  |  | FC-155 |  |  |  | FC-160 | [9 empty] | DA-210 |  |  |  | FA-215 |  |  |  | DA-220 |  |  |  | FA-225 |  |  |  | FA-223 | [12 empty] | DA-310 |  |  |  | FC-315 |  |  |  | FC-315 |  |  |  | HOLD |  |  |  | DA-320 |  |  |  | FA-325 |  |  |  | DA-330 |  |  |  | DA-350 |  |  |  | EA-351A |  |  |  | EA-351B |  |  |  | FA-354 |  |  |  | FC-355 |  |  |  | FC-355 |  |  |  | DA-360 |  |  |  | FA-365 |  |  |  | FA-371 |  |  |  | FA-373A |  |  |  | FA-373A |  |  |  | FA-373A |  |  |  | FA-415 |  |  |  | FA-781A |  |  |  | FA-781B |  |  |  | FC-812 |  |  |  | FA-815 |  |  |  | FA-830X |  |  |  | EA-830X |  |  |  | FA-860 |  |  |  | FB-835
4 |  | Line Class |  |  | FF59C |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BB57C1 |  |  |  | BB55C1 |  |  |  | BB55C1 | [9 empty] | BB57C1 |  |  |  | BB57C1 |  |  |  | BB57C1 |  |  |  | BB57C1 |  |  |  | BB55C1 | [12 empty] | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB57C1 |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1
5 |  | Nace Requirement
6 |  | Enclosure Class |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 | [9 empty] | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 | [12 empty] | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56
7
8 | SERVICE CONDITION | Fluid |  |  | DILUTE IPA |  |  |  | CAUSTIC 20 wt% |  |  |  | DILUTE IPA |  |  |  | RECYCLE GAS |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA | [9 empty] | PHE |  |  |  | PROPYLENE |  |  |  | PHE |  |  |  | PROPYLENE |  |  |  | PHE | [12 empty] | DILUTE IPA |  |  |  | WATER |  |  |  | HC |  |  |  | HOLD |  |  |  | WASH WATER |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA |  |  |  | IPA |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA |  |  |  | CYCLOHEXANE |  |  |  | SOLVENT |  |  |  | DILUTE IPA |  |  |  | PROCESS WATER |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA |  |  |  | IPA |  |  |  | IPA |  |  |  | IPA |  |  |  | PROPYLENE |  |  |  | DILUTE IPA |  |  |  | DILUTE IPA |  |  |  | CONDENSATE |  |  |  | CONDENSATE |  |  |  | POLISHED WATER |  |  |  | POLISHED WATER |  |  |  | DILUTE IPA |  |  |  | POLISHED WATER
9 |  | Flow Rate Unit |  | State | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | Nm3/h |  |  | V | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | [6 empty] | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | [9 empty] | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | HOLD |  |  | HOLD | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L
10 |  |  |  |  | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX | NOR | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX | NOR | MIN | MAX | NOR | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN
11 |  | Flow Rate | [110 empty] | '
12 |  | Pressure |  | (kg/cm2g) |  | 35.8 |  |  |  | ATM |  |  |  | HOLD |  |  |  | 44.8 |  |  |  | 31 |  |  |  | 31 |  |  |  | 31.6 |  |  |  | 16.8 |  |  |  | 0.2 |  |  |  | 0.2 | [9 empty] | 16.53 |  |  |  | 16.4 |  |  |  | 19.6 |  |  |  | 19 |  |  |  | 5.5 | [12 empty] | 0.25 |  |  |  | 0 |  |  |  | 0 |  |  |  | HOLD |  |  |  | 2 |  |  |  | 0.02 |  |  |  | 2.05 |  |  |  | 0.35 |  |  |  | 1.6 |  |  |  | 1.6 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0.33 |  |  |  | 0 |  |  |  | 0.03/0.02 |  |  |  | 0.03/0.02 |  |  |  | 0.03/0.02 |  |  |  | 0.03/0.02 |  |  |  | 15.2 |  |  |  | ATM |  |  |  | ATM |  |  |  | 3.5 |  |  |  | ATM |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 0.3 |  |  |  | ATM
13 |  | Temperature |  | (deg C) |  | 123.4 |  |  |  | 20 |  |  |  | HOLD |  |  |  | 120 |  |  |  | 94 |  |  |  | 94 |  |  |  | 94 |  |  |  | 93 |  |  |  | 82 |  |  |  | 77.9 | [9 empty] | 175.3 |  |  |  | 40 |  |  |  | 52.4 |  |  |  | 47 |  |  |  | 7 | [12 empty] | 97 |  |  |  | 45 |  |  |  | 45 |  |  |  | HOLD |  |  |  | 133.3 |  |  |  | 50 |  |  |  | 117.3 |  |  |  | 89.6 |  |  |  | 104.4 |  |  |  | 104.4 |  |  |  | 30 |  |  |  | 40 |  |  |  | 40 |  |  |  | 108 |  |  |  | 74 |  |  |  | 50 |  |  |  | 50 |  |  |  | 50 |  |  |  | 50 |  |  |  | AMB |  |  |  | AMB |  |  |  | AMB |  |  |  | 147 |  |  |  | 100 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | AMB |  |  |  | AMB
14 |  | Design Pressure |  | (kg/cm2g) | 55 |  |  |  | 0.5 |  |  |  | HOLD |  |  |  | 55 |  |  |  | 55 |  |  |  | 55 |  |  |  | 55 |  |  |  | 20 |  |  |  | 2 |  |  |  | 2 | [9 empty] | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 7.5 | [12 empty] | 2 |  |  |  | 2 |  |  |  | 2 |  |  |  | HOLD |  |  |  | 4 |  |  |  | 2 |  |  |  | 4 |  |  |  | 2 |  |  |  | 4 |  |  |  | 4 |  |  |  | 2 |  |  |  | 2 |  |  |  | HOLD |  |  |  | 2 |  |  |  | 2 |  |  |  | 0.5 / -0.1 |  |  |  | 0.5 / -0.1 |  |  |  | 0.5 / -0.1 |  |  |  | 0.5 / -0.1 |  |  |  | 25 |  |  |  | 0.5 / -0.1 |  |  |  | 0.5 / -0.1 |  |  |  | 6 |  |  |  | 2 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 2
15 |  | Design Temperatuer |  | (deg C) | 250 |  |  |  | 120 |  |  |  | HOLD |  |  |  | 180 |  |  |  | 150 |  |  |  | 150 |  |  |  | 150 |  |  |  | 140 |  |  |  | 120 |  |  |  | 120 | [9 empty] | 200 |  |  |  | 120 |  |  |  | 120 |  |  |  | 120 |  |  |  | 120 | [12 empty] | 150 |  |  |  | 120 |  |  |  | 120 |  |  |  | HOLD |  |  |  | 180 |  |  |  | 140 |  |  |  | 160 |  |  |  | 120 |  |  |  | 150 |  |  |  | 150 |  |  |  | 120 |  |  |  | 120 |  |  |  | HOLD |  |  |  | 140 |  |  |  | 120 |  |  |  | 120 |  |  |  | 120 |  |  |  | 120 |  |  |  | 120 |  |  |  | 65 / -15 |  |  |  | 120 |  |  |  | 120 |  |  |  | 200 |  |  |  | 150 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 300 |  |  |  | 120
16 |  | S.G. @ Op |  |  | 854.1 |  |  |  | 1220 |  |  |  | HOLD |  |  |  | 94.7 |  |  |  | 860 |  |  |  | 860 |  |  |  | 855.6228 |  |  |  | 848.6701 |  |  |  | 880.6614 |  |  |  | 739.1229 | [9 empty] | 485.9 |  |  |  | 454.3597 |  |  |  | 442.9 |  |  |  | 470 |  |  |  | 440 | [12 empty] | 901.6 |  |  |  | 970 |  |  |  | 690 |  |  |  | HOLD |  |  |  | 882.2 |  |  |  | 787.2 |  |  |  | 757.7 |  |  |  | 712.1 |  |  |  | 715.2 |  |  |  | 715.2 |  |  |  | 800 |  |  |  | 802 |  |  |  | 906 |  |  |  | 909.9 |  |  |  | 764.45 |  |  |  | 790 |  |  |  | 780 |  |  |  | 780 |  |  |  | 780 |  |  |  | 510 |  |  |  | 689 |  |  |  | 877 |  |  |  | 920 |  |  |  | 960 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 840 |  |  |  | 998
17 |  | Viscosity @ Op. |  |  | 0.214 |  |  |  | 5 |  |  |  | HOLD |  |  |  | 0.014233 |  |  |  | 0.0111 |  |  |  | 0.0111 |  |  |  | 0.28898 |  |  |  | 0.25004 |  |  |  | 0.25004 |  |  |  | 0.38061 | [9 empty] | 0.116 |  |  |  | 0.065 |  |  |  | 0.073 |  |  |  | 0.056 |  |  |  | HOLD | [12 empty] | 0.293 |  |  |  | 0.61 |  |  |  | 0.24 |  |  |  | HOLD |  |  |  | 0.2 |  |  |  | 0.848 |  |  |  | 0.229 |  |  |  | 0.419 |  |  |  | 0.298 |  |  |  | 0.298 |  |  |  | 0.73 |  |  |  | 0.73 |  |  |  | 0.71 |  |  |  | 0.257 |  |  |  | 0.456 |  |  |  | 1.34 |  |  |  | 0.7273 |  |  |  | 0.7273 |  |  |  | 0.7273 |  |  |  | 0.0803 |  |  |  | 0.258 |  |  |  | 0.771 |  |  |  | 0.18585 |  |  |  | 0.279 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 0.88997
18
19 | TRANSMITTER | Application |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL | [9 empty] | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL | [12 empty] | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL |  |  |  | LEVEL
20 |  | Mounting |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE | [9 empty] | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE | [12 empty] | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | REMOTE |  |  |  | DIRECT
21 |  | Adjustable Range |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD | [9 empty] | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD | [12 empty] | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
22 |  | Set Range |  | (mmH2O) | 0 ~ 1000 |  |  |  | 0 ~ 1440 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 0 ~ 800 |  |  |  | HOLD |  |  |  | 0 ~ 2300 |  |  |  | 0 ~ 5840 |  |  |  | 0 ~ 5840 |  |  |  | 0 ~ 600 | [9 empty] | 0 ~ 1200 |  |  |  | 0 ~ 1040 |  |  |  | 0 ~ 1200 |  |  |  | 0 ~ 1280 |  |  |  | 0 ~ 800 | [12 empty] | 0 ~ 3000 |  |  |  | 0 ~ 800 |  |  |  | 0 ~ 800 |  |  |  | HOLD |  |  |  | 0 ~ 3000 |  |  |  | 0 ~ 1600 |  |  |  | 0 ~ 1500 |  |  |  | 0 ~ 1400 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 0 ~ 2000 |  |  |  | 0 ~ 2600 |  |  |  | 0 ~ 2400 |  |  |  | 0 ~ 1200 |  |  |  | 0 ~ 1120 |  |  |  | 0 ~ 8500 |  |  |  | 0 ~ 8500 |  |  |  | 0 ~ 8500 |  |  |  | 0 ~ 8500 |  |  |  | 0 ~ 2000 |  |  |  | 0 ~ 8000 |  |  |  | 0 ~ 8000 |  |  |  | 0 ~ 2700 |  |  |  | 0 ~ 1800 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 0 ~ 500 |  |  |  | HOLD
23 |  | Scale Range
24 |  | Elevation / Suppression |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN | [9 empty] | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN | [12 empty] | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN |  |  |  | Within MAX. SPAN
25 |  | Element Type |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM | [9 empty] | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM | [12 empty] | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM
26 |  | Element Material |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS | [9 empty] | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS | [12 empty] | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS
27 |  | Body Material |  | Body Rating | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD | [7 empty] | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD | [10 empty] | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD |  | 316SS |  | MFR. STD
28 |  | Process Flanges Material |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS | [9 empty] | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS | [12 empty] | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS
29 |  | Wetted O-Rings Material |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD | [9 empty] | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD | [12 empty] | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
30 |  | Output Signal |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART | [9 empty] | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART | [12 empty] | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART |  |  |  | 4 ~ 20 mA HART
31 |  | Housing Material |  | Painting | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD | [7 empty] | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD | [10 empty] | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD |  | ALDC |  | MFR. STD
32 |  | Power Supply |  | Accuracy | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% | [7 empty] | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% | [10 empty] | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2% |  | LOOP PW |  | ±0.2%
33 |  | High Side: Conn. Size & Rating |  |  | 2" 600# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 600# RF |  |  |  | 2" 600# RF |  |  |  | 2" 600# RF |  |  |  | 2" 600# RF |  |  |  | 2" 300# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF | [9 empty] | 2" 300# RF |  |  |  | 2" 300# RF |  |  |  | 2" 300# RF |  |  |  | 2" 300# RF |  |  |  | 2" 150# RF | [12 empty] | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 300# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF
34 |  | Low Side: Conn. Size & Rating |  |  | 2" 600# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 600# RF |  |  |  | 2" 600# RF |  |  |  | 2" 600# RF |  |  |  | 2" 600# RF |  |  |  | 2" 300# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF | [9 empty] | 2" 300# RF |  |  |  | 2" 300# RF |  |  |  | 2" 300# RF |  |  |  | 2" 300# RF |  |  |  | 2" 150# RF | [12 empty] | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 300# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | 2" 150# RF |  |  |  | -
35 |  | Electriccal Connection |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT | [9 empty] | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT | [12 empty] | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT |  |  |  | 1/2" NPT
36
37 | DIAPHRAGM SEAL | Diaphragm Type |  | Extended Length | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH | [9 empty] | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH | [12 empty] | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH |  |  |  | FLUSH
38 |  | Diaphragm Material |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS | [9 empty] | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS | [12 empty] | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS |  |  |  | 316LSS
39 |  | Fill Fluid |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD | [9 empty] | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD | [12 empty] | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD |  |  |  | MFR. STD
40 |  | Capillary Material |  | Armor Material | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS | [7 empty] | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS | [10 empty] | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS |  | 316SS
41 |  | Capillary Type |  | Capillary Length | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m | [7 empty] | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m | [10 empty] | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 10 m |  | Amored |  | 10 m |  | Amored |  | 10 m |  | Amored |  | 10 m |  | Amored |  | 7 m |  | Amored |  | 10 m |  | Amored |  | 10 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m |  | Amored |  | 7 m
42 |  | Flush Ring |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) | [9 empty] | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) | [12 empty] | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT) |  |  |  | YES (1/2" NPT)
43
44 | ACCESSORIES | Display |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD | [9 empty] | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD | [12 empty] | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD |  |  |  | LCD
45 |  | Mounting Bracket |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE | [9 empty] | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE | [12 empty] | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | 2 inch PIPE |  |  |  | NO
46 |  | Hydrostatic Testing
47 |  | Valve Manifold Type
48 |  | Valve Manifold Material
49 |  | Special Cable
50
51
52 | PROQ. | Manufacturer
53 |  | Model
54
NOTE