## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | FIELD TRANSMITTER (TEMPERATURE) | [5 empty] | DS-IN-F-017D
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
FIELD TRANSMITTER
(TEMPERATURE)
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | JUL.16.'18 |  |  | FOR QUOTAION |  | J.H.Jung |  | C.M Lee | K.Y Noh |  |  | H.D.Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-017D |  |  | JUL.16.'18

## TEMP
[11 empty] | DATA SHEET | [12 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  |  | : M0556 | [5 empty] | FIELD TRANSMITTER (TEMPERATURE) | [12 empty] | DS-IN-F-017D
| PROJECT NAME |  |  |  | : IPA 50KTA Exp. | [18 empty] | REV. NO.
| LOCATION |  |  |  | : Yeosu, Korea | [18 empty] | A
1 | □ | COMPLETE ASSEMBLY | [6 empty] | □ | ELEMENT ONLY |  |  |  |  | TRANSMITTER
| □ | SEPARATED ASSEMBLY | [6 empty] | ■ | TRANSMITTER ONLY |  |  |  |  | 13 | DISPLAY |  |  | ■ | LCD |  |  |  | □ | BLIND
2 | ENCLOSURE |  |  | ■ | WEATHER PROOF | [6 empty] | IP 56 |  |  | 14 | METER SCALE |  |  | □ | 0 ~ 100 % |  |  |  | ■ | ACTUAL SCALE
|  |  |  | ■ | EXPLOSION PROOF | [6 empty] | Ex d IIB T4 |  |  | 15 | OUT PUT |  |  | ■ | 4 ~ 20 mA |  |  |  | ■ | HART
[15 empty] | 16 | POWER SUPPLY |  |  | ■ | 24V DC (LOOP) |  |  |  | □
ELEMENT | [14 empty] | 17 | LOSS OF INPUT |  |  | ■ | UPSCALE |  |  |  | □ | DOWNSCALE
3 | ELEMENT TYPE | [13 empty] | 18 | HOUSING MATERIAL | [5 empty] | MFR. STD
4 | ACCURACY | [13 empty] | 19 | ELECTRICAL CONNECTION | [5 empty] | 1/2" NPT
5 | SHEATH |  |  |  | MATERIAL | [6 empty] | O.D |  |  | 20 | INPUT SIGNAL | [5 empty] | RTD Pt 100 Ohm
[5 empty] | □ | SPRING LOADED | [8 empty] | 21 | ACCURACY | [5 empty] | ± 0.2 % OF CAL. SPAN
[5 empty] | □ | SINGLE |  |  |  |  | □ | DUPLEX |  |  | 22 | ACCESSORIES |  |  |  | 2" MOUNTING BRACKET ASSEMBLY
6 | NIPPLE |  |  |  | SIZE | [5 empty] | DIM. "N" | [8 empty] | SURGE PROTECTOR
[5 empty] | □ | UNION
7 | GROUNDING TYPE |  |  |  | □ | EXPOSED |  |  |  |  | □ | GROUNDED |  |  | WELL OR TUBE
[5 empty] | □ | UNGROUNDED | [8 empty] | 23 | MATERIAL
[15 empty] | 24 | CONSTRUCTION
HEAD | [14 empty] | 25 | PROCESS CONNECTION SIZE
8 | SCREW CAP & CHAIN | [6 empty] | □ | YES |  | □ | NO |  |  | 26 | DIMENSION |  |  | O.D |  |  |  |  | I.D
9 | MATERIAL | [6 empty] | □ | ALDC |  | □ |  |  |  | 27 | CHAIN & PLUG | [5 empty] | □ | YES | □ | NO
10 | ELECTRICAL CONNECTION | [13 empty] | 28 | ELEMENT CONNECTION
11 | WIRE QUANTITY | [13 empty] | 29 | MFR & MODEL NO.
12 | WIRE CONNECTION |  |  |  |  | □ | TERMINAL BLOCK |  |  |  |  | □ | LEAD WIRE |  | 30 | ■ | NAME PLATE (SS)
NO | TAG NO |  | SERVICE |  |  |  |  | P&ID |  |  | FLUID |  |  | DIM. "U" (mm) | CONN. RATING |  |  | CAL. RANGE (deg C) | PRESSURE (kg/cm2g) |  |  |  | TEMP. (deg C) |  |  | REMARK
DESIGN TEMP.
[19 empty] | MAX |  | NOR |  | MAX | NOR |  |  | LINE SIZE | LINE SPEC | NOZZLE PROJ | HOT | COLD | REMARK | HOLD POINT
1 | TT-1118 |  | DC-110 INLET |  |  |  |  | D-1-IPA-1001 |  |  | PRG (V) |  |  | - | - |  |  | 0 ~ 290 |  |  | 40 |  |  | 192 |  |  | 12" | BB59C1 |  | 280
2 | TT-1119 |  | DC-110 INLET |  |  |  |  | D-1-IPA-1001 |  |  | PRG (V) |  |  | - | - |  |  | 0 ~ 290 |  |  | 40 |  |  | 192 |  |  | 12" | BB59C1 |  | 280
3 | TT-1121 |  | EA-110 INLET |  |  |  |  | D-1-IPA-1001 |  |  | PRG (M) |  |  | - | - |  |  | 0 ~ 260 |  |  | 40.4 |  |  | 172.1 |  |  | 12" | BB59C1 |  | 280
4 | TT-1122 |  | DC-110 OUTLET |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 36.8 |  |  | 208 |  |  | 12" | BB59C1 |  | 250
5 | TT-1123 |  | EA-111 INLET |  |  |  |  | D-1-IPA-1001 |  |  | PRG (M) |  |  | - | - |  |  | 0 ~ 230 |  |  | 42.7 |  |  | 148.8 |  |  | 12" | FF59C |  | 250
6 | TT-1125 |  | EA-111 OUTLET |  |  |  |  | D-1-IPA-1001 |  |  | PRP (M) |  |  | - | - |  |  | 0 ~ 240 |  |  | 35.8 |  |  | 158.3 |  |  | 12" | BB59C1 |  | 250
7 | TT-1128 |  | EA-112 OUTLET |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 190 |  |  | 34.2 |  |  | 123.9 |  |  | 10" | FF59C |  | 150
8 | TT-1129 |  | PPF TO EA-112 |  |  |  |  | D-1-IPA-1001 |  |  | PPF (L) |  |  | - | - |  |  | 0 ~ 40 |  |  | 49.7 |  |  | 25(35) |  |  | 10" | FF59C |  | 65
9 | TT-1133 |  | EA-112 INLET |  |  |  |  | D-1-IPA-1001 |  |  | PRG (V) |  |  | - | - |  |  | 0 ~ 180 |  |  | 44.8 |  |  | 120 |  |  | 4" | BB59C1 |  | 180
10 | TT-1134 |  | EA-112 OUTLET |  |  |  |  | D-1-IPA-1001 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 33.1 |  |  | 40 |  |  | 10" | BB59C1 |  | 250
11 | TT-1135 |  | GA-115A/B DISCH. |  |  |  |  | D-1-IPA-1001 |  |  | PPW (L) |  |  | - | - |  |  | 0 ~ 160 |  |  | 49.8 |  |  | 102.9 |  |  | 3" | FF59C |  | 160
12 | TT-1136 |  | PPW TO EA-112 |  |  |  |  | D-1-IPA-1001 |  |  | PPW (L) |  |  | - | - |  |  | 0 ~ 160 |  |  | 49.5 |  |  | 102.9 |  |  | 3" | BB59C1 |  | 160
13 | TT-1142 |  | GB-120 SUCTION |  |  |  |  | D-1-IPA-1002 |  |  | PRG (V) |  |  | - | - |  |  | 0 ~ 150 |  |  | 31 |  |  | 94 |  |  | 3" | BB59C1 |  | 150
14 | TT-1145 |  | WW TO DA-140 INLET |  |  |  |  | D-1-IPA-1002 |  |  | PWW (L) |  |  | - | - |  |  | 0 ~ 150 |  |  | 39.3 |  |  | 95 |  |  | HOLD | HOLD |  | 150
15 | TT-1150 |  | DA-140 OUTLET |  |  |  |  | D-1-IPA-1002 |  |  | PRG (V) |  |  | - | - |  |  | 0 ~ 150 |  |  | 31.2 |  |  | 94.2 |  |  | 4" | BB59C1 |  | 150
16 | TT-1151 |  | EA-140A/B OUTLET |  |  |  |  | D-1-IPA-1002 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 50 |  |  | 5 |  |  | 32 |  |  | 12" | BB59C1 |  | 50
17 | TT-1152 |  | EA-140B OUTLET |  |  |  |  | D-1-IPA-1002 |  |  | PRP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 33.9 |  |  | 93.2 |  |  | 8" | BB55C |  | 150
18 | TT-1153 |  | EA-140A OUTLET |  |  |  |  | D-1-IPA-1002 |  |  | PRP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 33.9 |  |  | 93.2 |  |  | 8" | FF59C |  | 150
19 | TT-1154 |  | PRP TO DA-140 INLET |  |  |  |  | D-1-IPA-1002 |  |  | PRP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 33.9 |  |  | 93.2 |  |  | 8" | FF59C |  | 150
20 | TT-1155 |  | PRP TO DA-140 INLET |  |  |  |  | D-1-IPA-1002 |  |  | PRP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 33.9 |  |  | 93.2 |  |  | 10" | FF59C |  | 150
21 | TT-1157 |  | DA-140 OUTLET |  |  |  |  | D-1-IPA-1002 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 150 |  |  | 31.6 |  |  | 94 |  |  | 10" | FF59C |  | 150
22 | TT-1158 |  | DA-140 1ST BED |  |  |  |  | D-1-IPA-1002 |  |  | PDI / PRG (M) |  |  | - | - |  |  | 0 ~ 150 |  |  | 31.6 |  |  | 94 |  |  | 4" | BB59C1 |  | 150
23 | TT-1159 |  | DA-140 2ND BED |  |  |  |  | D-1-IPA-1002 |  |  | PDI / PRG (M) |  |  | - | - |  |  | 0 ~ 150 |  |  | 31.6 |  |  | 94 |  |  | HOLD | DA-140 |  | 150
24 | TT-1160 |  | FC-160 BED |  |  |  |  | D-1-IPA-1003 |  |  | PDI / PRG (M) |  |  | - | - |  |  | 0 ~ 120 |  |  | 0.2 |  |  | 78 |  |  | HOLD | DA-140 |  | 120
25 | TT-1161 |  | FC-160 |  |  |  |  | D-1-IPA-1003 |  |  | PRG (V) |  |  | - | - |  |  | 0 ~ 90 |  |  | 0.1 |  |  | 54 |  |  | HOLD | FC-160 |  | 120
26 | TT-1165 |  | EA-165 OUTLET |  |  |  |  | D-1-IPA-1003 |  |  | PRG (M) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0.1 |  |  | 38 |  |  | 4" | BB55C1 |  | 120
27 | TT-1210 |  | DA-210 |  |  |  |  | D-1-IPA-2001 |  |  | PHE (L) |  |  | - | - |  |  | 0 ~ 270 |  |  | 16.5 |  |  | 175 |  |  | 4" | BB55C1 |  | 200
28 | TT-1211 |  | DA-210 2ND BED |  |  |  |  | D-1-IPA-2001 |  |  | PHE (L) |  |  | - | - |  |  | 0 ~ 270 |  |  | 16.5 |  |  | 175 |  |  | HOLD | DA-210 |  | 200
29 | TT-1212 |  | DA-210 2ND BED |  |  |  |  | D-1-IPA-2001 |  |  | PRG (M) |  |  | - | - |  |  | 0 ~ 260 |  |  | 16.5 |  |  | 167.5 |  |  | HOLD | DA-210 |  | 200
30 | TT-1213 |  | DA-210 |  |  |  |  | D-1-IPA-2001 |  |  | PRG (V) |  |  | - | - |  |  | 0 ~ 70 |  |  | 16.5 |  |  | 41 |  |  | HOLD | DA-210 |  | 200
31 | TT-1215 |  | DA-210 OUTLET |  |  |  |  | D-1-IPA-2001 |  |  | PRG (V) |  |  | - | - |  |  | 0 ~ 70 |  |  | 16.5 |  |  | 41.2 |  |  | 6" | BB57C1 |  | 120
32 | TT-1216 |  | DA-210 1ST BED |  |  |  |  | D-1-IPA-2001 |  |  | PRG (M) |  |  | - | - |  |  | 0 ~ 70 |  |  | 16.5 |  |  | 42.8 |  |  | 6" | BB57C1 |  | 200
33 | TT-1217 |  | EA-215 OUTLET |  |  |  |  | D-1-IPA-2001 |  |  | PPR (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 16.4 |  |  | 39 |  |  | 4" | BB57C1 |  | 120
34 | TT-1218 |  | EA-215 WCR |  |  |  |  | D-1-IPA-2001 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 4.3 |  |  | 36 |  |  | 6" | BB55C |  | 50
35 | TT-1220 |  | DA-220 |  |  |  |  | D-1-IPA-2002 |  |  | PHE (L) |  |  | - | - |  |  | 0 ~ 80 |  |  | 19.6 |  |  | 52 |  |  | 6" | BB55C |  | 120
36 | TT-1221 |  | DA-220 3 STAGE |  |  |  |  | D-1-IPA-2002 |  |  | PHE / PPR (M) |  |  | - | - |  |  | 0 ~ 80 |  |  | 19.6 |  |  | 52 |  |  | - | DA-220 |  | 120
37 | TT-1223 |  | DA-220 |  |  |  |  | D-1-IPA-2002 |  |  | PPR (V) |  |  | - | - |  |  | 0 ~ 80 |  |  | 19.1 |  |  | 48 |  |  | HOLD | DA-220 |  | 120
38 | TT-1225 |  | WCR EA-225 OUTLET |  |  |  |  | D-1-IPA-2002 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 4.3 |  |  | 42 |  |  | 4" | BB55C |  | 50
39 | TT-1226 |  | EA-225 OUTLET |  |  |  |  | D-1-IPA-2002 |  |  | PPR (L) |  |  | - | - |  |  | 0 ~ 80 |  |  | 19 |  |  | 47.4 |  |  | 4" | BB55C |  | 120
40 | TT-1227 |  | FA-223 |  |  |  |  | D-1-IPA-2002 |  |  | PHE (L) |  |  | - | - |  |  | 0 ~ 20 |  |  | 5.5 |  |  | 7 |  |  | 4" | BB57C1 |  | 120
41 | TT-1228 |  | DA-220 |  |  |  |  | D-1-IPA-2002 |  |  | PHE (L) |  |  | - | - |  |  | 0 ~ 80 |  |  | 19.6 |  |  | 52 |  |  | HOLD | FA-223 |  | 120
42 | TT-1310 |  | DA-310 |  |  |  |  | D-1-IPA-3001 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.3 |  |  | 98 |  |  | - | DA-220 |  | 150
43 | TT-1311 |  | DA-310 10 STAGE |  |  |  |  | D-1-IPA-3001 |  |  | PDI (M) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.09 |  |  | 99 |  |  | HOLD | DA-310 |  | 150
44 | TT-1312 |  | WCR EA-316 OUTLET |  |  |  |  | D-1-IPA-3001 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 4.3 |  |  | 42 |  |  | 6" | BB55C |  | 50
45 | TT-1313 |  | EA-316 OUTLET LIQUID |  |  |  |  | D-1-IPA-3001 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 0.04 |  |  | 45 |  |  | 2" | BB55C1 |  | 150
46 | TT-1314 |  | DA-310 OUTLET |  |  |  |  | D-1-IPA-3001 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.05 |  |  | 94 |  |  | 2" | BB55C1 |  | 150
47 | TT-1315 |  | GA-315A/B DISCH. |  |  |  |  | D-1-IPA-3001 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.1 |  |  | 98 |  |  | 8" | BB55C1 |  | 150
48 | TT-1316 |  | DA-310 3 STAGE |  |  |  |  | D-1-IPA-3001 |  |  | PDI (M) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.24 |  |  | 95.7 |  |  | 3" | BB55C1 |  | 150
49 | TT-1317 |  | EA-316 OUTLET VAPOR |  |  |  |  | D-1-IPA-3001 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 70 |  |  | 0.04 |  |  | 45 |  |  | HOLD | HOLD |  | 150
50 | TT-1318 |  | EA-317 OUTLET TO FLARE |  |  |  |  | D-1-IPA-3001 |  |  | GFL (V) |  |  | - | - |  |  | 0 ~ 70 |  |  | 0 |  |  | 45 |  |  | 2" | BB55C1 |  | 150
51 | TT-1319 |  | WCR EA-317 OUTLET |  |  |  |  | D-1-IPA-3001 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 4.3 |  |  | 42 |  |  | 2" | BB55C |  | 50
52 | TT-1320 |  | DA-320 |  |  |  |  | D-1-IPA-3002 |  |  | PWW (L) |  |  | - | - |  |  | 0 ~ 200 |  |  | 2 |  |  | 133 |  |  | 1 1/2" | BB55C |  | 180
53 | TT-1321 |  | DA-320 3 STAGE |  |  |  |  | D-1-IPA-3002 |  |  | PWW (L) |  |  | - | - |  |  | 0 ~ 200 |  |  | 2 |  |  | 133 |  |  | HOLD | DA-320 |  | 180
54 | TT-1322 |  | DA-320 17 - 16 STAGE |  |  |  |  | D-1-IPA-3002 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 190 |  |  | 1.92 |  |  | 122.3 |  |  | HOLD | DA-320 |  | 180
55 | TT-1323 |  | DA-320 19 - 18 STAGE |  |  |  |  | D-1-IPA-3002 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 170 |  |  | 1.92 |  |  | 112.2 |  |  | HOLD | DA-320 |  | 180
56 | TT-1324 |  | DA-320 20 - 19 STAGE |  |  |  |  | D-1-IPA-3002 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 170 |  |  | 1.92 |  |  | 111 |  |  | HOLD | DA-320 |  | 180
57 | TT-1325 |  | DA-320 22 - 21 STAGE |  |  |  |  | D-1-IPA-3002 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 170 |  |  | 1.92 |  |  | 110.3 |  |  | HOLD | DA-320 |  | 180
58 | TT-1326 |  | DA-320 OUTLET |  |  |  |  | D-1-IPA-3002 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 160 |  |  | 1.6 |  |  | 106 |  |  | HOLD | DA-320 |  | 180
59 | TT-1327 |  | EA-320A/B/C OUTLET |  |  |  |  | D-1-IPA-3002 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 190 |  |  | 3.6 |  |  | 122 |  |  | 12" | BB55C1 |  | 180
60 | TT-XXXX |  | DA-320 |  |  |  |  | D-1-IPA-3002 |  |  | HOLD |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 6" | BB55C1 |  | HOLD
61 | TT-1329 |  | DA-320 17 - 16 STAGE |  |  |  |  | D-1-IPA-3002 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 190 |  |  | 1.92 |  |  | 122.3 |  |  | HOLD | DA-320 |  | 180
62 | TT-1330 |  | DA-330 4TH BED |  |  |  |  | D-1-IPA-3002 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 180 |  |  | 2.05 |  |  | 115.8 |  |  | HOLD | DA-320 |  | 160
63 | TT-1331 |  | DA-330 3 - 4 BED |  |  |  |  | D-1-IPA-3002 |  |  | PDI (M) |  |  | - | - |  |  | 0 ~ 170 |  |  | 2 |  |  | 112 |  |  | HOLD | DA-320 |  | 160
64 | TT-1332 |  | DA-330 2 - 3 BED |  |  |  |  | D-1-IPA-3002 |  |  | PDI (M) |  |  | - | - |  |  | 0 ~ 170 |  |  | 1.97 |  |  | 111.6 |  |  | HOLD | DA-320 |  | 160
65 | TT-1333 |  | DA-330 1 - 2 BED |  |  |  |  | D-1-IPA-3002 |  |  | PDI (M) |  |  | - | - |  |  | 0 ~ 170 |  |  | 1.93 |  |  | 111 |  |  | HOLD | DA-320 |  | 160
66 | TT-1335 |  | DA-330 OUTLET |  |  |  |  | D-1-IPA-3002 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 170 |  |  | 1.9 |  |  | 111 |  |  | HOLD | DA-320 |  | 160
67 | TT-1337 |  | DA-320 5 STAGE |  |  |  |  | D-1-IPA-3002 |  |  | PWW (L) |  |  | - | - |  |  | 0 ~ 200 |  |  | 2 |  |  | 133 |  |  | 6" | BB55C1 |  | 180
68 | TT-1340 |  | DA-340 2ND BED |  |  |  |  | D-1-IPA-3003 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 130 |  |  | 0.03 |  |  | 81 |  |  | HOLD | DA-320 |  | 150
69 | TT-1341 |  | DA-340 2 - 3 BED |  |  |  |  | D-1-IPA-3003 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 130 |  |  | 0.07 |  |  | 81.7 |  |  | HOLD | DA-340 |  | 150
70 | TT-1344 |  | EA-345 VENT TO FLARE |  |  |  |  | D-1-IPA-3003 |  |  | GFL (V) |  |  | - | - |  |  | 0 ~ 50 |  |  | 5 |  |  | 32 |  |  | HOLD | DA-340 |  | 50
71 | TT-1345 |  | EA-345 |  |  |  |  | D-1-IPA-3003 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 90 |  |  | 0.02 |  |  | 56 |  |  | 2" | BB55C |  | 150
72 | TT-1346 |  | EA-325 INLET |  |  |  |  | D-1-IPA-3003 |  |  | PDI (M) |  |  | - | - |  |  | 0 ~ 160 |  |  | 1.5 |  |  | 105 |  |  | 12" | BB55C1 |  | 180
73 | TT-1347 |  | WCR EA-325 OUTLET |  |  |  |  | D-1-IPA-3003 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 5 |  |  | 42 |  |  | 12" | BB55C1 |  | 50
74 | TT-1348 |  | EA-325 OUTLET |  |  |  |  | D-1-IPA-3003 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 80 |  |  | 1.5 |  |  | 50 |  |  | 8" | BB55C |  | 150
75 | TT-1350 |  | DA-350 |  |  |  |  | D-1-IPA-3004 |  |  | PIP (L) |  |  | - | - |  |  | 0 ~ 140 |  |  | 0.4 |  |  | 90 |  |  | 6" | BB55C1 |  | 120
76 | TT-1351A |  | EA-351A OUTLET |  |  |  |  | D-1-IPA-3004 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 160 |  |  | 1.6 |  |  | 104.4 |  |  | HOLD | DA-350 |  | 150
77 | TT-1351B |  | EA-351B OUTLET |  |  |  |  | D-1-IPA-3004 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 160 |  |  | 1.6 |  |  | 104.4 |  |  | 3" | BB55C1 |  | 150
78 | TT-1352 |  | DA-350 17 - 15 STAGE |  |  |  |  | D-1-IPA-3004 |  |  | PIP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 0.28 |  |  | 88 |  |  | 3" | BB55C1 |  | 120
79 | TT-1353 |  | EA-353A/B OUTLET |  |  |  |  | D-1-IPA-3004 |  |  | PIP (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0.003 |  |  | 40 |  |  | HOLD | DA-350 |  | 120
80 | TT-1354 |  | FA-354 |  |  |  |  | D-1-IPA-3004 |  |  | PS (L) |  |  | - | - |  |  | 0 ~ 50 |  |  | 0 |  |  | 30 |  |  | 2" | BB55C1 |  | 120
81 | TT-1355 |  | WCR EA-353A/B OUTLET |  |  |  |  | D-1-IPA-3004 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 2 |  |  | 42 |  |  | 4" | BB55C |  | 50
82 | TT-1356 |  | DA-350 61 - 59 STAGE |  |  |  |  | D-1-IPA-3004 |  |  | PIP (M) |  |  | - | - |  |  | 0 ~ 100 |  |  | 0.06 |  |  | 60.5 |  |  | 4" | BB55C |  | 120
83 | TT-1357 |  | DA-350 OUTLET |  |  |  |  | D-1-IPA-3004 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 120 |  |  | 0.1 |  |  | 75 |  |  | HOLD | DA-350 |  | 120
84 | TT-1359 |  | DA-350 22 - 19 STAGE |  |  |  |  | D-1-IPA-3004 |  |  | PIP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 0.26 |  |  | 87.5 |  |  | 16" | BB55C1 |  | 120
85 | TT-1360 |  | DA-350 37 STAGE |  |  |  |  | D-1-IPA-3004 |  |  | PIP (M) |  |  | - | - |  |  | 0 ~ 130 |  |  | 0.17 |  |  | 82.6 |  |  | HOLD | DA-350 |  | 120
86 | TT-1361 |  | DA-350 24 STAGE |  |  |  |  | D-1-IPA-3004 |  |  | PIP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 0.24 |  |  | 87 |  |  | HOLD | DA-350 |  | 120
87 | TT-1362 |  | DA-350 12 STAGE |  |  |  |  | D-1-IPA-3004 |  |  | PIP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 0.28 |  |  | 88.5 |  |  | HOLD | DA-350 |  | 120
88 | TT-1363 |  | DA-350 4 STAGE |  |  |  |  | D-1-IPA-3004 |  |  | PIP (M) |  |  | - | - |  |  | 0 ~ 140 |  |  | 0.34 |  |  | 89.3 |  |  | HOLD | DA-350 |  | 120
89 | TT-13600 |  | DA-360 |  |  |  |  | D-1-IPA-3006 |  |  | PPW (L) |  |  | - | - |  |  | 0 ~ 160 |  |  | 0.3 |  |  | 108 |  |  | HOLD | DA-350 |  | 140
90 | TT-13601 |  | DA-360 17 STAGE |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.25 |  |  | 97.8 |  |  | HOLD | DA-360 |  | 140
91 | TT-13602 |  | DA-360 MIDDLE |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.19 |  |  | 96.5 |  |  | HOLD | DA-360 |  | 140
92 | TT-13603 |  | DA-360 13 STAGE |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 160 |  |  | 0.27 |  |  | 106.6 |  |  | HOLD | DA-360 |  | 140
93 | TT-13604 |  | DA-360 |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 120 |  |  | 0.06 |  |  | 80 |  |  | HOLD | DA-360 |  | 140
94 | TT-13605 |  | DA-360 3 STAGE |  |  |  |  | D-1-IPA-3006 |  |  | PPW (L) |  |  | - | - |  |  | 0 ~ 170 |  |  | 0.32 |  |  | 107.8 |  |  | HOLD | DA-360 |  | 140
95 | TT-13606 |  | DA-360 52 - 50 STAGE |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.08 |  |  | 94.1 |  |  | HOLD | DA-360 |  | 140
96 | TT-13607 |  | DA-360 54 - 52 STAGE |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 150 |  |  | 0.07 |  |  | 93.8 |  |  | HOLD | DA-360 |  | 140
97 | TT-13608 |  | DA-360 56 - 54 STAGE |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 140 |  |  | 0.06 |  |  | 91.1 |  |  | HOLD | DA-360 |  | 140
98 | TT-1366 |  | DA-360 OUTLET |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 140 |  |  | 0.06 |  |  | 91.1 |  |  | HOLD | DA-360 |  | 140
99 | TT-1367 |  | EA-365 GAS OUTLET |  |  |  |  | D-1-IPA-3006 |  |  | PDI (V) |  |  | - | - |  |  | 0 ~ 130 |  |  | 0.1 |  |  | 80.3 |  |  | 12" | BB55C1 |  | 120
100 | TT-1368 |  | EA-365 LIQUID OUTLET |  |  |  |  | D-1-IPA-3006 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 120 |  |  | 0.04 |  |  | 73.7 |  |  | 2" | BB55C1 |  | 120
101 | TT-1369 |  | WCR EA-365 OUTLET |  |  |  |  | D-1-IPA-3006 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 2 |  |  | 42 |  |  | 2" | BB55C1 |  | 50
102 | TT-1375 |  | PURE IPA TO DT-420A/B |  |  |  |  | D-1-IPA-3007 |  |  | PIP (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 4.66 |  |  | 40 |  |  | 6" | BB55C |  | 120
103 | TT-1381 |  | EA-327 VENT TO FLARE |  |  |  |  | D-1-IPA-3003 |  |  | VA (V) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0.01 |  |  | 40 |  |  | 4" | BB55C1 |  | 150
104 | TT-1382 |  | WCR EA-327 OUTLET |  |  |  |  | D-1-IPA-3003 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 5 |  |  | 42 |  |  | 2" | BB55C |  | 50
105 | TT-1383 |  | EA-327 OUTLET |  |  |  |  | D-1-IPA-3003 |  |  | PDI (-) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0.01 |  |  | 40 |  |  | 1" | BB55C |  | 150
106 | TT-1384 |  | EA-324 OUTLET |  |  |  |  | D-1-IPA-3003 |  |  | WW (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 4.3 |  |  | 40 |  |  | 1" | BB55C1 |  | 150
107 | TT-1385 |  | WCR EA-324 OUTLET |  |  |  |  | D-1-IPA-3003 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 2 |  |  | 40 |  |  | 4" | BB55C1 |  | 50
108 | TT-1386 |  | PWW EA-323 OUTLET |  |  |  |  | D-1-IPA-3003 |  |  | PWW (L) |  |  | - | - |  |  | 0 ~ 150 |  |  | 5 |  |  | 97.9 |  |  | 6" | BB55C |  | 150
109 | TT-1387 |  | DEMI WATER EA-323A/B OUTLET |  |  |  |  | D-1-IPA-3003 |  |  | WT (L) |  |  | - | - |  |  | 0 ~ 120 |  |  | 5.7 |  |  | 75.9 |  |  | 6" | BB55C1 |  | 160
110 | TT-1388 |  | FB-835 |  |  |  |  | D-1-IPA-8013 |  |  | WT (L) |  |  | - | - |  |  | 0 ~ 30 |  |  | 6 |  |  | 20 |  |  | 3" | BB55C1 |  | 150
111 | TT-1389 |  | PWW TO DA-310 |  |  |  |  | D-1-IPA-3003 |  |  | PWW (L) |  |  | - | - |  |  | 0 ~ 150 |  |  | 5 |  |  | 97.9 |  |  | HOLD | BB55C1 |  | 150
112 | TT-1390 |  | PWW TO DA-310 |  |  |  |  | D-1-IPA-3003 |  |  | PWW (L) |  |  | - | - |  |  | 0 ~ 150 |  |  | 5 |  |  | 97.9 |  |  | 4" | BB55C1 |  | 150
113 | TT-1391 |  | DEMI WATER TO EA-812 |  |  |  |  | D-1-IPA-3003 |  |  | PWW (L) |  |  | - | - |  |  | 0 ~ 120 |  |  | 5.7 |  |  | 75.9 |  |  | 4" | BB55C1 |  | 160
114 | TT-1395A |  | EA-355 OUTLET |  |  |  |  | D-1-IPA-3005 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0.003 |  |  | 40 |  |  | 3" | BB55C1 |  | 120
115 | TT-1396A |  | WCR EA-355 OUTLET |  |  |  |  | D-1-IPA-3005 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 2 |  |  | 40 |  |  | 6" | BB55C1 |  | 50
116 | TT-1397 |  | EA-357 OUTLET |  |  |  |  | D-1-IPA-3005 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0.003 |  |  | 40 |  |  | 10" | BB55C |  | 120
117 | TT-1398 |  | EA-357 TO FC-355 |  |  |  |  | D-1-IPA-3005 |  |  | GFL (V) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0.003 |  |  | 40 |  |  | 2" | BB55C1 |  | 120
118 | TT-1399 |  | WCR EA-357 OUTLET |  |  |  |  | D-1-IPA-3005 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 2 |  |  | 42 |  |  | 2" | BB55C |  | 50
119 | TT-1401 |  | PPR FROM GA-410A/B |  |  |  |  | D-1-IPA-4001 |  |  | PPR (L) |  |  | - | - |  |  | 0 ~ 40 |  |  | 18 |  |  | 25(35) |  |  | 1 1/2" | BB55C |  | HOLD
120 | TT-1410 |  | FA-415 |  |  |  |  | D-1-IPA-4001 |  |  | PPR (L) |  |  | - | - |  |  | 0 ~ 80 |  |  | 15.2 |  |  | AMB |  |  | 2" | BB57C1 |  | 65
121 | TT-1411 |  | FA-415 OUTLET |  |  |  |  | D-1-IPA-4001 |  |  | PPF (L) |  |  | - | - |  |  | 0 ~ 40 |  |  | 15.2 (18.89) |  |  | 25(35) |  |  | 4" | BB57C1 |  | 65
122 | TT-1415 |  | FA-415 OUTLET |  |  |  |  | D-1-IPA-4001 |  |  | PPF (L) |  |  | - | - |  |  | 0 ~ 40 |  |  | 15.39 (18.89) |  |  | 25(35) |  |  | 4" | BB57C1 |  | 65
123 | TT-1420A |  | FB-420A |  |  |  |  | D-1-IPA-4002 |  |  | PIP (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0 |  |  | 40 |  |  | 4" | BB57C1 |  | 120
124 | TT-1420B |  | FB-420B |  |  |  |  | D-1-IPA-4002 |  |  | PIP (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 0 |  |  | 40 |  |  | HOLD | FB-420A |  | 120
125 | TT-1435 |  | NS FROM GA-982XC |  |  |  |  | D-1-IPA-4003 |  |  | WT (L) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 3/4" | BB55C1 |  | HOLD
126 | TT-1801 |  | HP FROM B.L |  |  |  |  | D-1-IPA-8011 |  |  | HS (S) |  |  | - | - |  |  | 0 ~ 560 |  |  | 40 |  |  | 370 |  |  | 3/4" | BB55C1 |  | 425
127 | TT-1802 |  | BFW FROM B.L |  |  |  |  | D-1-IPA-8011 |  |  | BFW (L) |  |  | - | - |  |  | 0 ~ 120 |  |  | 64.6 |  |  | 80 |  |  | 6" | BA59C |  | HOLD
128 | TT-1803 |  | CONDENSATE TO B.L |  |  |  |  | D-1-IPA-8011 |  |  | CL (L) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 1 1/2" | HOLD |  | HOLD
129 | TT-1805 |  | MSS TO BG-803 |  |  |  |  | D-1-IPA-8011 |  |  | MSS (S) |  |  | - | - |  |  | 0 ~ 340 |  |  | 14.6 |  |  | 226 |  |  | 3" | BB55C |  | HOLD
130 | TT-1807 |  | MSS TO BG-803 |  |  |  |  | D-1-IPA-8011 |  |  | MSS (S) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 10" | BB57C |  | HOLD
131 | TT-1811 |  | BG-801 OUTLET |  |  |  |  | D-1-IPA-8011 |  |  | SH (S) |  |  | - | - |  |  | 0 ~ 390 |  |  | 31 |  |  | 255 |  |  | 10" | BB57C |  | 400
132 | TT-1812 |  | BG-802 OUTLET |  |  |  |  | D-1-IPA-8011 |  |  | SM (S) |  |  | - | - |  |  | 0 ~ 300 |  |  | 9.8 |  |  | 198 |  |  | 6" | BA59C |  | 250
133 | TT-1813 |  | WT EA-812 OUTLET |  |  |  |  | D-1-IPA-8011 |  |  | WT (L) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 10" | BB57C |  | HOLD
134 | TT-1814 |  | SL TO CONSUMER |  |  |  |  | D-1-IPA-8011 |  |  | SL (S) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 3" | BB55C1 |  | HOLD
135 | TT-1815 |  | EA-815 TO ATM. |  |  |  |  | D-1-IPA-8011 |  |  | VA (V) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 6" | BB55C |  | HOLD
136 | TT-1816 |  | WCR EA-815 OUTLET |  |  |  |  | D-1-IPA-8011 |  |  | WCR (L) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 2" | BB55C |  | HOLD
137 | TT-1818 |  | CL TO BG-802, BG-803 |  |  |  |  | D-1-IPA-8011 |  |  | CL (L) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 6" | BB55C |  | HOLD
138 | TT-1820 |  | CWS GA-820A/B DISCH. |  |  |  |  | D-1-IPA-8012 |  |  | WCS (L) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 1 1/2" | BB55C |  | HOLD
139 | TT-1821 |  | CWR EF-820 INLET |  |  |  |  | D-1-IPA-8012 |  |  | WCR (L) |  |  | - | - |  |  | 0 ~ 70 |  |  | 2 |  |  | 42 |  |  | 18" | BB55C |  | 50
140 | TT-1830 |  | FA-830X |  |  |  |  | D-1-IPA-8013 |  |  | WT (L) |  |  | - | - |  |  | HOLD |  |  | HOLD |  |  | HOLD |  |  | 18" | BB55C |  | HOLD
141 | TT-1839 |  | WT FROM B.L |  |  |  |  | D-1-IPA-8013 |  |  | WT (L) |  |  | - | - |  |  | 0 ~ 80 |  |  | 5 |  |  | AMB |  |  | 3" | BB55C1 |  | AMB
142 | TT-1842 |  | AI FROM BL |  |  |  |  | D-1-IPA-8014 |  |  | AI (V) |  |  | - | - |  |  | 0 ~ 80 |  |  | 7 |  |  | AMB |  |  | 3" | BB55C1 |  | 60
143 | TT-1847 |  | NL FROM BL |  |  |  |  | D-1-IPA-8014 |  |  | NL (V) |  |  | - | - |  |  | 0 ~ 80 |  |  | 7 |  |  | AMB |  |  | 4" | BC55C |  | 60
144 | TT-1860 |  | FA-860 |  |  |  |  | D-1-IPA-8023 |  |  | PDI (L) |  |  | - | - |  |  | 0 ~ 80 |  |  | 0.3 |  |  | AMB |  |  | 3" | BB55C |  | 300
145 | TT-1870 |  | AP FROM B.L |  |  |  |  | D-1-IPA-8015 |  |  | AP (V) |  |  | - | - |  |  | 0 ~ 80 |  |  | 7 |  |  | AMB |  |  | 3" | BB55C |  | 60
146 | TT-1880 |  | WR FROM B.L |  |  |  |  | D-1-IPA-8022 |  |  | WR (L) |  |  | - | - |  |  | 0 ~ 80 |  |  | 4 |  |  | AMB |  |  | 3" | BB55C |  | 60
147 | TT-1890 |  | WW FROM EA-324 |  |  |  |  | D-1-IPA-8024 |  |  | WW (L) |  |  | - | - |  |  | 0 ~ 60 |  |  | 4.19 |  |  | 40 |  |  | 4" | BB55C |  | 150

## TEMP(MULTI)
[11 empty] | DATA SHEET | [12 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  |  | : M0556 | [5 empty] | FIELD TRANSMITTER (TEMPERATURE) | [12 empty] | DS-IN-F-017D
| PROJECT NAME |  |  |  | : IPA 50KTA Exp. | [18 empty] | REV. NO.
| LOCATION |  |  |  | : Yeosu, Korea | [18 empty] | A
1 | □ | COMPLETE ASSEMBLY | [6 empty] | □ | ELEMENT ONLY |  |  |  |  | TRANSMITTER
| □ | SEPARATED ASSEMBLY | [6 empty] | ■ | TRANSMITTER ONLY |  |  |  |  | 13 | DISPLAY |  |  | ■ | LCD |  |  |  | □ | BLIND
2 | ENCLOSURE |  |  | □ | WEATHER PROOF | [6 empty] | IP 56 |  |  | 14 | METER SCALE |  |  | □ | 0 ~ 100 % |  |  |  | ■ | ACTUAL SCALE
|  |  |  | □ | EXPLOSION PROOF | [6 empty] | Ex d IIB T4 |  |  | 15 | OUT PUT |  |  | ■ | 4 ~ 20 mA |  |  |  | ■ | HART
[15 empty] | 16 | POWER SUPPLY |  |  | ■ | 24V DC (LOOP) |  |  |  | □
ELEMENT | [14 empty] | 17 | LOSS OF INPUT |  |  | ■ | UPSCALE |  |  |  | □ | DOWNSCALE
3 | ELEMENT TYPE | [13 empty] | 18 | HOUSING MATERIAL | [5 empty] | MFR. STD
4 | ACCURACY | [13 empty] | 19 | ELECTRICAL CONNECTION | [5 empty] | 1/2" NPT
5 | SHEATH |  |  |  | MATERIAL | [6 empty] | O.D |  |  | 20 | INPUT SIGNAL | [5 empty] | RTD Pt 100 Ohm
[5 empty] | □ | SPRING LOADED | [8 empty] | 21 | ACCURACY | [5 empty] | ± 0.2 % OF CAL. SPAN
[5 empty] | □ | SINGLE |  |  |  |  | ■ | DUPLEX |  |  | 22 | ACCESSORIES |  |  |  | SURGE PROTECTOR
6 | NIPPLE |  |  |  | SIZE | [5 empty] | DIM. "N"
[5 empty] | □ | UNION
7 | GROUNDING TYPE |  |  |  | □ | EXPOSED |  |  |  |  | □ | GROUNDED |  |  | WELL OR TUBE
[5 empty] | □ | UNGROUNDED | [8 empty] | 23 | MATERIAL
[15 empty] | 24 | CONSTRUCTION
HEAD | [14 empty] | 25 | PROCESS CONNECTION SIZE
8 | SCREW CAP & CHAIN | [6 empty] | □ | YES |  | □ | NO |  |  | 26 | DIMENSION |  |  | O.D |  |  |  |  | I.D
9 | MATERIAL | [6 empty] | □ | ALDC |  | □ |  |  |  | 27 | CHAIN & PLUG | [5 empty] | □ | YES | □ | NO
10 | ELECTRICAL CONNECTION | [13 empty] | 28 | ELEMENT CONNECTION
11 | WIRE QUANTITY | [13 empty] | 29 | MFR & MODEL NO.
12 | WIRE CONNECTION |  |  |  |  | □ | TERMINAL BLOCK |  |  |  |  | □ | LEAD WIRE |  | 30 | □ | NAME PLATE (SS)
NO | TAG NO |  | SERVICE |  |  |  |  | P&ID |  |  | FLUID |  |  | DIM. "U" (mm) | CONN. RATING |  |  | CAL. RANGE (deg C) | PRESSURE (kg/cm2g) |  |  |  | TEMP. (deg C) |  |  | REMARK
DESIGN TEMP.
[19 empty] | MAX |  | NOR |  | MAX | NOR |  |  | LINE SIZE | LINE SPEC | NOZZLE PROJ | HOT | COLD | REMARK | HOLD POINT
1 | TT-1112A |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
2 | TT-1112B |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
3 | TT-1112C |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
4 | TT-1112D |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
5 | TT-1112E |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
6 | TT-1112F |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
7 | TT-1112G |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
8 | TT-1112H |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
9 | TT-1112I |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280
10 | TT-1112J |  | DC-110 |  |  |  |  | D-1-IPA-1001 |  |  | PRP (V) |  |  | - | - |  |  | 0 ~ 320 |  |  | 40 |  |  | 208 |  | DIN RAIL | HOLD | DC-110 |  | 280