## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | LOCAL INSTRUMENT (TEMPERATURE GAUGE) | [5 empty] | DS-IN-F-018B
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
TEMPERATURE GAUGE
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | AUG.16.'18 |  |  | FOR QUOTAION |  | J.H.Jung |  | C.M Lee | K.Y Noh |  |  | H.D.Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-018B |  |  | 2018.08.16

## DATA SHEET
[9 empty] | DATA SHEET | [11 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  |  | : M0556 |  |  |  | LOCAL INSTRUMENT (TEMPERATURE GAUGE) | [11 empty] | DS-IN-F-018B
| PROJECT NAME |  |  |  | : IPA 50KTA Exp. | [15 empty] | REV. NO.
| LOCATION |  |  |  | : Yeosu, Korea | [15 empty] | A
1. | ■ | COMPLETE ASSEMBLY |  |  |  |  | □ | THERMOMETER ONLY | [5 empty] | WELL OR TUBE
| □ | WELL ONLY | [11 empty] | 11. | MATERIAL |  |  |  |  | 316SS
[14 empty] | 12. | CONSTRUCTION |  |  |  |  | DRILLED & TAPERED
ELEMENT | [13 empty] | 13. | PROCESS CONNECTION SIZE |  |  |  |  | 1-1/2"
2. | STEM |  | □ | THREADED |  | □ | PLAIN |  |  | ■ | UNION |  |  | 14. | DIMENSION |  | O.D | 23 / 19 mm |  |  | I.D |  | 7 mm
3. | STEM OR UNION THREAD |  |  |  |  | 1/2" NPT | [7 empty] | 15. | CHAIN & PLUG |  |  |  | □ | YES | ■ | NO
4. | STEM DIAMETER |  |  |  |  | 6.4 mm | [7 empty] | 16. | ELEMENT CONNECTION |  |  |  |  | 1/2" NPT
5. | CASE MATERIAL |  |  |  |  | 304SS | [7 empty] | 17. | WELL CALCULATION |  |  | ASME PTC 19.3 part 3 (Latest Ver.)
6. | DIAL SIZE |  |  |  | 100 mm |  | COLOR |  |  | WHITE BOARD |  |  |  | 18. | MFR & MODEL NO.
7. | SCALE LENGTH |  |  |  | MFR. STD |  | COLOR |  |  | BLACK LETTER
8. | FORM |  | ■ | ADJUSTABLE |  | □ | BACK |  |  | □ | BOTTOM |  |  | NOTE
9. | OPTION |  | ■ | EXTERNAL CLIBRATION
|  |  | □ | HERMETICALLY SEAL CASE
10. | ACCURACY |  |  |  |  | 1 % OF READING
NO | TAG NO |  | SERVICE |  |  | P&ID |  |  | FLUID |  |  |  | DIM. "U" (mm) | CONN. RATING |  | CAL. RANGE (deg C) | PRESSURE (kg/cm2g) |  |  | TEMP. (deg C) |  |  | REMARK
DESIGN TEMP.
[9 empty] | NAME |  |  | P |  |  |  |  | MAX | NOR |  | MAX | NOR |  |  | LINE SIZE | LINE SPEC | NOZZLE PROJ | HOT | COLD
1 | TG-1134 |  | TO FA-134 |  |  | D-1-IPA-0004-2 |  |  | PRG |  |  | L | 200 | 150# RF |  | 0 ~ 50 |  | 0.5 |  |  | 25 |  |  | 1" | FF55C | 1 1/2" | 60
2 | TG-1140 |  | GB-120 DISCHARGE |  |  | D-1-IPA-1002 |  |  | PRG |  |  | V | 250 | 600# RF |  | 0 ~ 190 |  | 47 |  |  | 125 |  |  | 6" | BB59C1 | 1 1/2" | 180
3 | TG-1142 |  | GB-120 SUCTION |  |  | D-1-IPA-1002 |  |  | PRG |  |  | V | 300 | 600# RF |  | 0 ~ 140 |  | 31 |  |  | 94 |  |  | 12" | BB59C1 | 1 1/2" | 150
4 | TG-1158 |  | FC-150 OUTLET |  |  | D-1-IPA-1003 |  |  | PDI |  |  | L | 200 | 300# RF |  | 0 ~ 140 |  | 16.8 |  |  | 93 |  |  | 4" | BB57C1 | 1 1/2" | 140
5 | TG-1159 |  | FC-155 OUTLET |  |  | D-1-IPA-1003 |  |  | PDI |  |  | L | 250 | 150# RF |  | 0 ~ 130 |  | 0.4 |  |  | 82.4 |  |  | 6" | BB55C1 | 1 1/2" | 120
6 | TG-1162 |  | FC-160 BTM. OUTLET |  |  | D-1-IPA-1003 |  |  | PDI |  |  | L | 200 | 150# RF |  | 0 ~ 120 |  | 0.69 |  |  | 77.7 |  |  | 2" | BB55C1 | 1 1/2" | 120
7 | TG-1166 |  | WCR EA-165 OUTLET |  |  | D-1-IPA-1003 |  |  | WCR |  |  | L | 250 | 150# RF |  | 0 ~ 70 |  | 4.3 |  |  | 42 |  |  | 6" | BB55C | 1 1/2" | 50
8 | TG-1219 |  | EA-217 OUTLET |  |  | D-1-IPA-2001 |  |  | PRG |  |  | V | 200 | 300# RF |  | 0 ~ 60 |  | 16.4 |  |  | 39 |  |  | 1" | BB57C1 | 1 1/2" | 120
9 | TG-1224 |  | PHE TO FA-223 |  |  | D-1-IPA-2002 |  |  | PHE |  |  | L | 200 | 300# RF |  | 0 ~ 80 |  | 19.6 |  |  | 52 |  |  | 1" | BB57C1 | 1 1/2" | 120
10 | TG-1328 |  | EA-320A/B/C OUTLET |  |  | D-1-IPA-3002 |  |  | PWW |  |  | L | 250 | 150# RF |  | 0 ~ 160 |  | 5.65 |  |  | 106.9 |  |  | 6" | BB55C1 | 1 1/2" | 180
11 | TG-1336 |  | EA-333 TO WWT |  |  | D-1-IPA-3002 |  |  | PDI |  |  | L | 200 | 150# RF |  | 0 ~ 60 |  | 1.95 |  |  | 40 |  |  | 1" | BB55C1 | 1 1/2" | 160
12 | TG-1412 |  | PPR FROM GA-410A/B |  |  | D-1-IPA-4001 |  |  | PPR |  |  | L | 200 | 300# RF |  | 0 ~ 50 |  | 18 |  | 35 | 25 |  |  | 3" | BA8A | 1 1/2" | 65 | -15
13 | TG-1420A |  | FB-420A EQUIPMENT |  |  | D-1-IPA-4002 |  |  | PIP |  |  | L | 400 | 150# RF |  | 0 ~ 50 |  | ATM |  |  | AMB |  |  | VESSEL | BB55C1 | 1 1/2" | 120
14 | TG-1420B |  | FB-420B EQUIPMENT |  |  | D-1-IPA-4002 |  |  | PIP |  |  | L | 400 | 150# RF |  | 0 ~ 50 |  | ATM |  |  | AMB |  |  | VESSEL | BB55C1 | 1 1/2" | 120
15 | TG-1435 |  | NS FROM GA-982XC |  |  | D-1-IPA-4003 |  |  | NS |  |  | L | 200 | 150# RF |  | 0 ~ 60 |  | 7.7 |  |  | 40 |  |  | 1 1/2" | BB55C1 | 1 1/2" | 120
16 | TG-1801 |  | HP STEAM FROM B.L |  |  | D-1-IPA-8011 |  |  | HS |  |  | S | 250 | 600# RF |  | 0 ~ 560 |  | 40 |  |  | 370 |  |  | 6" | BA59C | 1 1/2" | 425
17 | TG-1802 |  | BFW FROM B.L |  |  | D-1-IPA-8011 |  |  | BFW |  |  | L | 200 | 600# RF |  | 0 ~ 130 |  | 64.6 |  |  | 80 |  |  | 1 1/2" | BA59C | 1 1/2" | 300
18 | TG-1805 |  | MSS TO BG-803 |  |  | D-1-IPA-8011 |  |  | MSS |  |  | S | 250 | 300# RF |  | 0 ~ 340 |  | 14.6 |  |  | 226 |  |  | 10" | BB57C | 1 1/2" | 350
19 | TG-1820 |  | GA-820A/B DISCH. |  |  | D-1-IPA-8012 |  |  | WCS |  |  | L | 350 | 150# RF |  | 0 ~ 50 |  | 5.5 |  |  | 32 |  |  | 18" | BB55C | 1 1/2" | AMB
20 | TG-1821 |  | WCR TO EF-820 |  |  | D-1-IPA-8012 |  |  | WCR |  |  | L | 350 | 150# RF |  | 0 ~ 70 |  | 2 |  |  | 42 |  |  | 18" | BB55C | 1 1/2" | 50
21 | TG-1830 |  | FA-830X EQUIPMENT |  |  | D-1-IPA-8013 |  |  | WT |  |  | L | 400 | 150# RF |  | 0 ~ 160 |  | 0.25 |  | 120 | 105 |  |  | VESSEL | BB55C1 | 1 1/2" | 180
22 | TG-1831 |  | EA-830X EQUIPMENT |  |  | D-1-IPA-8013 |  |  | WT |  |  | L | 400 | 150# RF |  | 0 ~ 160 |  | 0.75 |  |  | 106.8 |  |  | VESSEL | BB55C1 | 1 1/2" | 180
23 | TG-1833 |  | DA-830 TO EA-830X |  |  | D-1-IPA-8013 |  |  | CM |  |  | V | 200 | 300# RF |  | 0 ~ 240 | 8 | 2.5 |  | 193.5 | 143.5 |  |  | 4" | BB57C | 1 1/2" | 250
24 | TG-1834 |  | EA-830X TO CM / CL |  |  | D-1-IPA-8013 |  |  | CM |  |  | L | 200 | 300# RF |  | 0 ~ 240 | 8 | 2.5 |  | 193.5 | 143.5 |  |  | 1 1/2" | BB57C | 1 1/2" | 250
25 | TG-1842 |  | AI FROM B.L |  |  | D-1-IPA-8014 |  |  | AI |  |  | V | 200 | 150# RF |  | 0 ~ 50 |  | 7 |  |  | AMB |  |  | 4" | BC55C | 1 1/2" | 60
26 | TG-1847 |  | NL FROM B.L |  |  | D-1-IPA-8014 |  |  | NL |  |  | V | 200 | 150# RF |  | 0 ~ 50 |  | 7 |  |  | AMB |  |  | 4" | BB55C | 1 1/2" | 60
27 | TG-1860 |  | FA-860 EQUIPMENT |  |  | D-1-IPA-8023-1 |  |  | PDI |  |  | L | 400 | 150# RF |  | 0 ~ 50 |  | 0.3 |  |  | AMB |  |  | VESSEL | BB55C1 | 1 1/2" | 300
28 | TG-1870 |  | PLNAT AIR FROM B.L |  |  | D-1-IPA-8015 |  |  | AP |  |  | V | 200 | 150# RF |  | 0 ~ 50 |  | 7 |  |  | AMB |  |  | 3" | BB55C | 1 1/2" | 60
29 | TG-1880 |  | WR FROM B.L |  |  | D-1-IPA-8022 |  |  | WR |  |  | L | 200 | 150# RF |  | 0 ~ 50 |  | 4 |  |  | AMB |  |  | 4" | BB55C | 1 1/2" | 60

## Sheet1
NO | TAG NO | SERVICE | P&ID | FLUID |  | DIM. "U" (mm) | CONN. RATING | CAL. RANGE (deg C) |  |  | PRESSURE (kg/cm2g) |  | TEMP. (deg C) |  | REMARK
DESIGN TEMP.
|  |  |  | NAME | P | [5 empty] | MAX | NOR | MAX | NOR |  | LINE SIZE | LINE SPEC | NOZZLE PROJ | HOT | COLD | 1.5
1 | TG-1134 | TO FA-134 | D-1-IPA-0004-2 | PRG | L | 200 | 150# RF | 0 ~ 50 | 0 | 50 |  | 0.5 |  | 25 |  | 1" | FF55C | 1 1/2" | 60 |  | 37.5 | 0.5
12 | TG-1412 | PPR FROM GA-410A/B | D-1-IPA-4001 | PPR | L | 200 | 300# RF | 0 ~ 50 | 0 | 50 |  | 18 | 35 | 25 |  | 3" | BA8A | 1 1/2" | 65 | -15 | 37.5 | 0.5
19 | TG-1820 | GA-820A/B DISCH. | D-1-IPA-8012 | WCS | L | 350 | 150# RF | 0 ~ 50 | 0 | 50 |  | 5.5 |  | 32 |  | 18" | BB55C | 1 1/2" | AMB |  | 48 | 0.64
8 | TG-1219 | EA-217 OUTLET | D-1-IPA-2001 | PRG | V | 200 | 300# RF | 0 ~ 60 | 0 | 60 |  | 16.4 |  | 39 |  | 1" | BB57C1 | 1 1/2" | 120 |  | 58.5 | 0.65
11 | TG-1336 | EA-333 TO WWT | D-1-IPA-3002 | PDI | L | 200 | 150# RF | 0 ~ 60 | 0 | 60 |  | 1.95 |  | 40 |  | 1" | BB55C1 | 1 1/2" | 160 |  | 60 | 0.66667
15 | TG-1435 | NS FROM GA-982XC | D-1-IPA-4003 | NS | L | 200 | 150# RF | 0 ~ 60 | 0 | 60 |  | 7.7 |  | 40 |  | 1 1/2" | BB55C1 | 1 1/2" | 120 |  | 60 | 0.66667
7 | TG-1166 | WCR EA-165 OUTLET | D-1-IPA-1003 | WCR | L | 250 | 150# RF | 0 ~ 70 | 0 | 70 |  | 4.3 |  | 42 |  | 6" | BB55C | 1 1/2" | 50 |  | 63 | 0.6
20 | TG-1821 | WCR TO EF-820 | D-1-IPA-8012 | WCR | L | 350 | 150# RF | 0 ~ 70 | 0 | 70 |  | 2 |  | 42 |  | 18" | BB55C | 1 1/2" | 50 |  | 63 | 0.6
9 | TG-1224 | PHE TO FA-223 | D-1-IPA-2002 | PHE | L | 200 | 300# RF | 0 ~ 80 | 0 | 80 |  | 19.6 |  | 52 |  | 1" | BB57C1 | 1 1/2" | 120 |  | 78 | 0.65
6 | TG-1162 | FC-160 BTM. OUTLET | D-1-IPA-1003 | PDI | L | 200 | 150# RF | 0 ~ 120 | 0 | 120 |  | 0.69 |  | 77.7 |  | 2" | BB55C1 | 1 1/2" | 120 |  | 116.55 | 0.6475
17 | TG-1802 | BFW FROM B.L | D-1-IPA-8011 | BFW | L | 200 | 600# RF | 0 ~ 130 | 0 | 130 |  | 64.6 |  | 80 |  | 1 1/2" | BA59C | 1 1/2" | 300 |  | 120 | 0.61538
5 | TG-1159 | FC-155 OUTLET | D-1-IPA-1003 | PDI | L | 250 | 150# RF | 0 ~ 130 | 0 | 130 |  | 0.4 |  | 82.4 |  | 6" | BB55C1 | 1 1/2" | 120 |  | 123.6 | 0.63385
4 | TG-1158 | FC-150 OUTLET | D-1-IPA-1003 | PDI | L | 200 | 300# RF | 0 ~ 140 | 0 | 140 |  | 16.8 |  | 93 |  | 4" | BB57C1 | 1 1/2" | 140 |  | 139.5 | 0.66429
3 | TG-1142 | GB-120 SUCTION | D-1-IPA-1002 | PRG | V | 300 | 600# RF | 0 ~ 140 | 0 | 140 |  | 31 |  | 94 |  | 12" | BB59C1 | 1 1/2" | 150 |  | 141 | 0.67143
21 | TG-1830 | FA-830X EQUIPMENT | D-1-IPA-8013 | WT | L | 400 | 150# RF | 0 ~ 160 | 0 | 160 |  | 0.25 | 120 | 105 |  | VESSEL | BB55C1 | 1 1/2" | 180 |  | 157.5 | 0.65625
22 | TG-1831 | EA-830X EQUIPMENT | D-1-IPA-8013 | WT | L | 400 | 150# RF | 0 ~ 160 | 0 | 160 |  | 0.75 |  | 106.8 |  | VESSEL | BB55C1 | 1 1/2" | 180 |  | 160.2 | 0.6675
10 | TG-1328 | EA-320A/B/C OUTLET | D-1-IPA-3002 | PWW | L | 250 | 150# RF | 0 ~ 160 | 0 | 160 |  | 5.65 |  | 106.9 |  | 6" | BB55C1 | 1 1/2" | 180 |  | 160.35 | 0.66813
2 | TG-1140 | GB-120 DISCHARGE | D-1-IPA-1002 | PRG | V | 250 | 600# RF | 0 ~ 190 | 0 | 190 |  | 47 |  | 125 |  | 6" | BB59C1 | 1 1/2" | 180 |  | 187.5 | 0.65789
23 | TG-1833 | DA-830 TO EA-830X | D-1-IPA-8013 | CM | V | 200 | 300# RF | 0 ~ 240 | 0 | 240 | 8 | 2.5 | 193.5 | 143.5 |  | 4" | BB57C | 1 1/2" | 250 |  | 215.25 | 0.59792
24 | TG-1834 | EA-830X TO CM / CL | D-1-IPA-8013 | CM | L | 200 | 300# RF | 0 ~ 240 | 0 | 240 | 8 | 2.5 | 193.5 | 143.5 |  | 1 1/2" | BB57C | 1 1/2" | 250 |  | 215.25 | 0.59792
18 | TG-1805 | MSS TO BG-803 | D-1-IPA-8011 | MSS | S | 250 | 300# RF | 0 ~ 340 | 0 | 340 |  | 14.6 |  | 226 |  | 10" | BB57C | 1 1/2" | 350 |  | 339 | 0.66471
16 | TG-1801 | HP STEAM FROM B.L | D-1-IPA-8011 | HS | S | 250 | 600# RF | 0 ~ 560 | 0 | 560 |  | 40 |  | 370 |  | 6" | BA59C | 1 1/2" | 425 |  | 555 | 0.66071
13 | TG-1420A | FB-420A EQUIPMENT | D-1-IPA-4002 | PIP | L | 400 | 150# RF | 0 ~ 50 | 0 | 50 |  | ATM |  | AMB |  | VESSEL | BB55C1 | 1 1/2" | 120 |  | #VALUE! | #VALUE!
14 | TG-1420B | FB-420B EQUIPMENT | D-1-IPA-4002 | PIP | L | 400 | 150# RF | 0 ~ 50 | 0 | 50 |  | ATM |  | AMB |  | VESSEL | BB55C1 | 1 1/2" | 120 |  | #VALUE! | #VALUE!
25 | TG-1842 | AI FROM B.L | D-1-IPA-8014 | AI | V | 200 | 150# RF | 0 ~ 50 | 0 | 50 |  | 7 |  | AMB |  | 4" | BC55C | 1 1/2" | 60 |  | #VALUE! | #VALUE!
26 | TG-1847 | NL FROM B.L | D-1-IPA-8014 | NL | V | 200 | 150# RF | 0 ~ 50 | 0 | 50 |  | 7 |  | AMB |  | 4" | BB55C | 1 1/2" | 60 |  | #VALUE! | #VALUE!
27 | TG-1860 | FA-860 EQUIPMENT | D-1-IPA-8023-1 | PDI | L | 400 | 150# RF | 0 ~ 50 | 0 | 50 |  | 0.3 |  | AMB |  | VESSEL | BB55C1 | 1 1/2" | 300 |  | #VALUE! | #VALUE!
28 | TG-1870 | PLNAT AIR FROM B.L | D-1-IPA-8015 | AP | V | 200 | 150# RF | 0 ~ 50 | 0 | 50 |  | 7 |  | AMB |  | 3" | BB55C | 1 1/2" | 60 |  | #VALUE! | #VALUE!
29 | TG-1880 | WR FROM B.L | D-1-IPA-8022 | WR | L | 200 | 150# RF | 0 ~ 50 | 0 | 50 |  | 4 |  | AMB |  | 4" | BB55C | 1 1/2" | 60 |  | #VALUE! | #VALUE!

## Sample (hidden)
[9 empty] | DATA SHEET | [11 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  |  | : M0526 |  |  |  | LOCAL INSTRUMENT (TEMPERATURE GAUGE) | [11 empty] | DS-IM-018C
| PROJECT NAME |  |  |  | : CA2 150KT Exp. | [15 empty] | REV. NO.
| LOCATION |  |  |  | : Yeosu, Korea | [15 empty] | A
1. | ■ | COMPLETE ASSEMBLY |  |  |  |  | □ | THERMOMETER ONLY | [5 empty] | WELL OR TUBE
| □ | WELL ONLY | [11 empty] | 11. | MATERIAL |  |  |  |  | 316SS
[14 empty] | 12. | CONSTRUCTION |  |  |  |  | DRILLED & TAPERED
ELEMENT | [13 empty] | 13. | PROCESS CONNECTION SIZE |  |  |  |  | 1-1/2"
2. | STEM |  | □ | THREADED |  | □ | PLAIN |  |  | ■ | UNION |  |  | 14. | DIMENSION |  | O.D | 23 / 19 mm |  |  | I.D |  | 7 mm
3. | STEM OR UNION THREAD |  |  |  |  | 1/2" NPT | [7 empty] | 15. | CHAIN & PLUG |  |  |  | □ | YES | ■ | NO
4. | STEM DIAMETER |  |  |  |  | 6.4 mm | [7 empty] | 16. | ELEMENT CONNECTION |  |  |  |  | 1/2" NPT
5. | CASE MATERIAL |  |  |  |  | 304SS | [7 empty] | 17. | WELL CALCULATION |  |  | ASME PTC 19.3 part 3 (Latest Ver.)
6. | DIAL SIZE |  |  |  | 100 mm |  | COLOR |  |  | WHITE BOARD |  |  |  | 18. | MFR & MODEL NO.
7. | SCALE LENGTH |  |  |  | MFR. STD |  | COLOR |  |  | BLACK LETTER
8. | FORM |  | ■ | ADJUSTABLE |  | □ | BACK |  |  | □ | BOTTOM |  |  | NOTE
9. | OPTION |  | ■ | EXTERNAL CLIBRATION
|  |  | □ | HERMETICALLY SEAL CASE
10. | ACCURACY |  |  |  |  | 1 % OF READING
NO | TAG NO |  | SERVICE |  |  | P&ID |  |  | FLUID |  |  |  | DIM. "U" (mm) | CONN. RATING |  | CAL. RANGE (deg C) | PRESSURE (kg/cm2g) |  |  | TEMP. (deg C) |  |  | REMARK
DESIGN TEMP.
[9 empty] | NAME |  |  | P |  |  |  |  | MAX | NOR |  | MAX | NOR |  |  | LINE SIZE | LINE SPEC | NOZZLE PROJ | HOT | COLD | REMARK
1 | TG-0121A |  | DISCH. 012-JA |  |  | 64-D0900 |  |  | CW |  |  | L | 350 | 150# RF |  | 0 ~ 80 | - | 6.95 |  | 37 | 32 |  |  | 34" | LG
2 | TG-0121B |  | DISCH. 012-JB |  |  | 64-D0900 |  |  | CW |  |  | L | 350 | 150# RF |  | 0 ~ 80 | - | 6.95 |  | 37 | 32 |  |  | 34" | LG
3 | TG-0121C |  | DISCH. 012-JC |  |  | 64-D0900 |  |  | CW |  |  | L | 350 | 150# RF |  | 0 ~ 80 | - | 6.95 |  | 37 | 32 |  |  | 34" | LG
4 | TG-0128 |  | HW HEADER |  |  | 64-D0900 |  |  | HW |  |  | L | 350 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 44" | LC |  |  |  | LC, PIT 확인
5 | TG-0129A |  | HW TO COOLING TOWER |  |  | 64-D0900 |  |  | HW |  |  | L | 350 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 40" | LG
6 | TG-0129B |  | HW TO COOLING TOWER |  |  | 64-D0900 |  |  | HW |  |  | L | 350 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 40" | LG
7 | TG-0129C |  | HW TO COOLING TOWER |  |  | 64-D0900 |  |  | HW |  |  | L | 350 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 40" | LG
8 | TG-03911 |  | 0391-D |  |  | 62-D1304 |  |  | OIL+POWDER |  |  | L | 400 | 150# RF |  | 0 ~ 100 | - | 6 |  | - | AMB |  | Well Mat'l : 316LSS | - | 0391-D | 160 mm
9 | TG-06106 |  | HW FROM 0602-C |  |  | 62-D0601 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 10" | LG
10 | TG-06206 |  | HW FROM 0608-C |  |  | 62-D0602 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 6" | LG
11 | TG-06210 |  | BR RETURN FROM 0612-C |  |  | 62-D0602 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3 |  | - | 10 |  |  | 8" | LG
12 | TG-06213 |  | HW FROM 0617-C |  |  | 62-D0602 |  |  | HW |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 3" | LG
13 | TG-06306 |  | 0603-D |  |  | 62-D0604 |  |  | SOL.+POLYMER |  |  | L | 400 | 300# RF |  | 0 ~ 250 | - | 0.1 ~ 0.818 |  | 144.4 | - |  |  | - | 0603-D | 202 mm
14 | TG-06307 |  | HW FROM 0605-C |  |  | 62-D0604 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 8" | LG
15 | TG-06308 |  | HW FROM 0607-C |  |  | 62-D0604 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 6" | LG
16 | TG-06310 |  | HW FROM 0606-C |  |  | 62-D0604 |  |  | HW |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 4" | LG
17 | TG-06311 |  | HW FROM PIPE H.E. |  |  | 62-D0604 |  |  | HW |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 2" | LG
18 | TG-06502 |  | HW FROM 0616-C |  |  | 62-D0610 |  |  | HW |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 4" | LG
19 | TG-08101 |  | BR SUPPLY TO 0801-F VENT |  |  | 62-D0800 |  |  | BR SUPPLY |  |  | L | 200 | 150# RF |  | -20 ~ 50 | - | 5 |  | 10 | 0 |  |  | 2" HOLD | LG
20 | TG-08102 |  | BR RETURN FROM 0801-F VENT |  |  | 62-D0800 |  |  | BR RETURN |  |  | L | 200 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 5 |  |  | 2" HOLD | LG
21 | TG-08103 |  | BR SUPPLY TO 0802-F VENT |  |  | 62-D0800 |  |  | BR SUPPLY |  |  | L | 200 | 150# RF |  | -20 ~ 50 | - | 5 |  | 10 | 0 |  |  | 2" HOLD | LG
22 | TG-08104 |  | BR RETURN FROM 0802-F VENT |  |  | 62-D0800 |  |  | BR RETURN |  |  | L | 200 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 5 |  |  | 2" HOLD | LG
23 | TG-08200 |  | 0820-F |  |  | 62-D0303 |  |  | BR |  |  | L | 400 | 150# RF |  | -20 ~ 50 | - | ATM |  | 20 | 10 |  |  | - | 0820-F | 170 mm
24 | TG-08206 |  | 0801-D |  |  | 62-D1803 |  |  | HOT OIL |  |  | L | 600 | 300# RF |  | 0 ~ 350 | - | 0.1 |  | 290 | 120 |  |  | - | 0801-D | 377 mm
25 | TG-08281 |  | HOT OIL OUTLET FROM 0801-C |  |  | 62-D1803 |  |  | HOT OIL |  |  | L | 350 | 300# RF |  | 0 ~ 350 | - | 6.36 |  | 190 | 180 |  |  | 18" | HO
26 | TG-09407 |  | 0910-D |  |  | 62-D0901 |  |  | CONDENSATE |  |  | L | 500 | 150# RF |  | 0 ~ 150 | - | ATM |  | 110 | 70 ~ 95 |  |  | - | 0910-D | 218 mm
27 | TG-09409 |  | HW FROM 0910-C |  |  | 62-D0901 |  |  | HW |  |  | L | 300 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 40 |  |  | 14" | LG
28 | TG-09410 |  | HW FROM 0911-C |  |  | 62-D0901 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 40 |  |  | 10" | LG
1 | TG-11907 |  | 1907-D |  |  | 62-D1900 |  |  | CLEANING OIL |  |  | L | 400 | 300# RF |  | 0 ~ 300 | - | ATM |  | 200 | 160 |  |  | - | 1907-D | 160 mm
2 | TG-12014A |  | SEAL FLUSH TO 1201-JA |  |  | 62-D0004 |  |  | SOLVENT |  |  | L | 200 | 600# RF |  | 0 ~ 100 | 40 | 19.9 |  | - | 46.5 |  |  | 1/2" | D
3 | TG-12014B |  | SEAL FLUSH TO 1201-JB |  |  | 62-D0004 |  |  | SOLVENT |  |  | L | 200 | 600# RF |  | 0 ~ 100 | 40 | 19.9 |  | - | 46.5 |  |  | 1/2" | D
4 | TG-12081A |  | PUMP SEAL FOR 1208-JA |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
5 | TG-12081B |  | PUMP SEAL FOR 1208-JB |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
6 | TG-12121A |  | PUMP SEAL FOR 1212-JA |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
7 | TG-12121B |  | PUMP SEAL FOR 1212-JB |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
8 | TG-12211A |  | PUMP SEAL FOR 1221-JA |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
9 | TG-12211B |  | PUMP SEAL FOR 1221-JB |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
10 | TG-12217A |  | HW FROM 1217-CA |  |  | 62-D1207 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 10" | LG
11 | TG-12217B |  | HW FROM 1217-CB |  |  | 62-D1207 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 10" | LG
12 | TG-12223 |  | HW FROM 1201-C |  |  | 62-D1203 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 37 |  |  | 6" | LG
13 | TG-12224 |  | CW / BR FROM 1203-C |  |  | 62-D1203 |  |  | HW / BR RETURN |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.00 ~ 3.50 |  | 45 | 37 |  |  | 6" | LG
14 | TG-12225 |  | BR FROM 1205-C |  |  | 62-D1203 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 6" | LG
15 | TG-12304 |  | BR FROM 1222-C |  |  | 62-D1101 |  |  | BR RETURN |  |  | L | 200 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 1 1/2" | LG
16 | TG-12462A |  | HW FROM 1206-CA |  |  | 62-D1208 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 38 |  |  | 10" | LG
17 | TG-12462B |  | HW FROM 1206-CB |  |  | 62-D1208 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 38 |  |  | 10" | LG
18 | TG-12462C |  | HW FROM 1206-CC |  |  | 62-D1208 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 38 |  |  | 10" | LG
19 | TG-12465A |  | BR FROM 1207-CA |  |  | 62-D1208 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 10" | LG
20 | TG-12465B |  | BR FROM 1207-CB |  |  | 62-D1208 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 10" | LG
21 | TG-12468A |  | BR FROM 1208-CA |  |  | 62-D1207 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 10" | LG
22 | TG-12468B |  | BR FROM 1208-CB |  |  | 62-D1207 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 10" | LG
23 | TG-12601 |  | 1210-D |  |  | 62-D1211 |  |  | ADD.+HEXANE |  |  | L | 300 | 300# RF |  | 0 ~ 150 | - | ATM |  | 130 | 30 |  |  | - | 1210-D | 165 mm |  |  | 내부 coil support <-> Internal Wall 150 mm ?
24 | TG-12602 |  | 1209-D |  |  | 62-D1211 |  |  | ADDITIVES |  |  | L | 300 | 300# RF |  | 0 ~ 150 | - | ATM |  | 130 | 30 |  |  | - | 1209-D | 165 mm |  |  | 내부 coil support <-> Internal Wall 150 mm ?
25 | TG-12611 |  | TW FROM 1210-D |  |  | 62-D1211 |  |  | TW RETURN |  |  | L | 200 | 150# RF |  | 0 ~ 200 | - | 5.5 |  | 140 | 32 |  |  | 2" | AA
26 | TG-12612 |  | TW FROM 1209-D |  |  | 62-D1211 |  |  | TW RETURN |  |  | L | 200 | 150# RF |  | 0 ~ 200 | - | 5.5 |  | 140 | 32 |  |  | 2" | AA
27 | TG-13011 |  | VENT FROM 1301-V |  |  | 62-D1300-02 |  |  | SOLVENT+POE |  |  | V | 200 | 150# RF |  | HOLD | - | HOLD |  | - | HOLD |  | ADDED | 3" | AA
28 | TG-13227 |  | HW FROM 1306-JA/B INLET LINE |  |  | 62-D1300 |  |  | HW |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 2" | LG
29 | TG-13402A |  | HW FROM 1301-CA |  |  | 62-D1305 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 8" | LG
30 | TG-13402B |  | HW FROM 1301-CB |  |  | 62-D1305 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 8" | LG
31 | TG-13506 |  | HW FROM EXTRUDER |  |  | 62-D1300-12 |  |  | HW |  |  | L | 400 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 2" | LG
32 | TG-13921 |  | 1392-D |  |  | 62-D1304 |  |  | OIL+POWDER |  |  | L | 400 | 150# RF |  | 0 ~ 100 | - | 1.5 |  | - | AMB |  | Well Mat'l : 316LSS | - | 1392-D | 160 mm |  |  | AGITATOR 간섭 확인
33 | TG-17110 |  | BR FROM 1701-C |  |  | 62-D1700 |  |  | BR RETURN |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3 |  | - | 10 |  |  | 3" | LG
34 | TG-19101 |  | 1906-D |  |  | 62-D1900 |  |  | CLEANING OIL |  |  | L | 400 | 300# RF |  | 0 ~ 300 | - | ATM |  | 200 | 160 |  |  | - | 1906-D | 160 mm
35 | TG-19102 |  | CLEANING OIL SUPPPLY |  |  | 62-D1900 |  |  | CLEANING OIL |  |  | L | 250 | 300# RF |  | 0 ~ 300 | - | 5 |  | 200 | 160 |  |  | 6" | B
36 | TG-19104 |  | HW TO 1906-D/1907-D OVHD |  |  | 62-D1900 |  |  | HW |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 2" | LG
37 | TG-19202 |  | OUTLET TW MIXING TEE |  |  | 62-D1211 |  |  | TW |  |  | L | 200 | 150# RF |  | 0 ~ 200 | - | 5.5 |  | 140 | 32 |  |  | 4" | AF
38 | TG-19503 |  | HW FROM 1201-L |  |  | 64-D1902 |  |  | HW |  |  | L | 300 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 16" | LC
1 | TG-21907 |  | 2907-D |  |  | 62-D2900 |  |  | CLEANING OIL |  |  | L | 400 | 300# RF |  | 0 ~ 300 | - | ATM |  | 200 | 160 |  |  | - | 2907-D
2 | TG-22014A |  | SEAL FLUSH TO 1201-JA |  |  | 62-D0004 |  |  | SOLVENT |  |  | L | 200 | 600# RF |  | 0 ~ 100 | 40 | 19.9 |  | - | 46.5 |  |  | 1/2" | D
3 | TG-22014B |  | SEAL FLUSH TO 1201-JB |  |  | 62-D0004 |  |  | SOLVENT |  |  | L | 200 | 600# RF |  | 0 ~ 100 | 40 | 19.9 |  | - | 46.5 |  |  | 1/2" | D
4 | TG-22081A |  | PUMP SEAL FOR 2208-JA |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
5 | TG-22081B |  | PUMP SEAL FOR 2208-JB |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
6 | TG-22121A |  | PUMP SEAL FOR 2212-JA |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
7 | TG-22121B |  | PUMP SEAL FOR 2212-JB |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
8 | TG-22211A |  | PUMP SEAL FOR 2221-JA |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
9 | TG-22211B |  | PUMP SEAL FOR 2221-JB |  |  | 62-D0004-01 |  |  | SOLVENT |  |  | L | 200 | 300# RF |  | 0 ~ 200 | 16 | 14.5 |  | - | 135 |  |  | 1/2" | B
10 | TG-22217A |  | HW FROM 2217-CA |  |  | 62-D2207 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 10" | LG
11 | TG-22217B |  | HW FROM 2217-CB |  |  | 62-D2207 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 10" | LG
12 | TG-22223 |  | HW FROM 2201-C |  |  | 62-D2203 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 36 |  |  | 6" | LG
13 | TG-22224 |  | HW / BR FROM 2203-C |  |  | 62-D2203 |  |  | HW / BR RETURN |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.00 ~ 3.50 |  | 45 | 37 |  |  | 6" | LG
14 | TG-22225 |  | BR FROM 2205-C |  |  | 62-D2203 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 6" | LG
15 | TG-22304 |  | BR FROM 2222-C |  |  | 62-D2101 |  |  | BR RETURN |  |  | L | 200 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 1 1/2" | LG
16 | TG-22462A |  | HW FROM 2206-CA |  |  | 62-D2208 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 38 |  |  | 10" | LG
17 | TG-22462B |  | HW FROM 2206-CB |  |  | 62-D2208 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 38 |  |  | 10" | LG
18 | TG-22462C |  | HW FROM 2206-CC |  |  | 62-D2208 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 38 |  |  | 10" | LG
19 | TG-22465A |  | BR FROM 2207-CA |  |  | 62-D2208 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 10" | LG
20 | TG-22465B |  | BR FROM 2207-CB |  |  | 62-D2208 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 10" | LG
21 | TG-22468A |  | BR FROM 2208-CA |  |  | 62-D2207 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 10" | LG
22 | TG-22468B |  | BR FROM 2208-CB |  |  | 62-D2207 |  |  | BR RETURN |  |  | L | 250 | 150# RF |  | -20 ~ 50 | - | 3 |  | 15 | 10 |  |  | 10" | LG
23 | TG-22601 |  | 2210-D |  |  | 62-D2211 |  |  | ADD.+HEXANE |  |  | L | 300 | 300# RF |  | 0 ~ 150 | - | ATM |  | 130 | 30 |  |  | - | 2210-D | 165 mm |  |  | 내부 coil support <-> Internal Wall 150 mm ?
24 | TG-22602 |  | 2209-D |  |  | 62-D2211 |  |  | ADDITIVES |  |  | L | 300 | 300# RF |  | 0 ~ 150 | - | ATM |  | 130 | 30 |  |  | - | 2209-D | 165 mm |  |  | 내부 coil support <-> Internal Wall 150 mm ?
25 | TG-22611 |  | TW FROM 2210-D |  |  | 62-D2211 |  |  | TW RETURN |  |  | L | 200 | 150# RF |  | 0 ~ 200 | - | 5.5 |  | 140 | 32 |  |  | 2" | AA
26 | TG-22612 |  | TW FROM 2209-D |  |  | 62-D2211 |  |  | TW RETURN |  |  | L | 200 | 150# RF |  | 0 ~ 200 | - | 5.5 |  | 140 | 32 |  |  | 2" | AA
27 | TG-23011 |  | VENT FROM 2301-V |  |  | 62-D2300-02 |  |  | SOLVENT+POE |  |  | V | 200 | 150# RF |  | HOLD | - | HOLD |  | - | HOLD |  | ADDED | 3" | AA
28 | TG-23227 |  | HW FROM 2306-JA/B INLET LINE |  |  | 62-D2300 |  |  | HW |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 2" | LG
29 | TG-23402A |  | HW FROM 2301-CA |  |  | 62-D2305 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 8" | LG
30 | TG-23402B |  | HW FROM 2301-CB |  |  | 62-D2305 |  |  | HW |  |  | L | 250 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 8" | LG
31 | TG-23506 |  | HW FROM EXTRUDER |  |  | 62-D1300-12 |  |  | HW |  |  | L | 400 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | - | 38 |  |  | 2" | LG
32 | TG-23921 |  | 2392-D |  |  | 62-D2304 |  |  | OIL+POWDER |  |  | L | 400 | 150# RF |  | 0 ~ 100 | - | 1.5 |  | - | AMB |  | Well Mat'l : 316LSS | - | 2392-D | 160 mm |  |  | AGITATOR 간섭 확인
33 | TG-27110 |  | BR FROM 2701-C |  |  | 62-D2700 |  |  | BR RETURN |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3 |  | - | 10 |  |  | 3" | LG
34 | TG-29101 |  | 2906-D |  |  | 62-D2900 |  |  | CLEANING OIL |  |  | L | 400 | 300# RF |  | 0 ~ 300 | - | ATM |  | 200 | 160 |  |  | - | 2906-D | 160 mm
35 | TG-29102 |  | CLEANING OIL SUPPPLY |  |  | 62-D2900 |  |  | CLEANING OIL |  |  | L | 250 | 300# RF |  | 0 ~ 300 | - | 5 |  | 200 | 160 |  |  | 6" | B
36 | TG-29104 |  | HW TO 1906-D/1907-D OVHD |  |  | 62-D2900 |  |  | HW |  |  | L | 200 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 2" | LG
37 | TG-29202 |  | OUTLET TW MIXING TEE |  |  | 62-D2211 |  |  | TW |  |  | L | 200 | 150# RF |  | 0 ~ 200 | - | 5.5 |  | 140 | 32 |  |  | 4" | AF
38 | TG-29503 |  | HW FROM 2201-L |  |  | 64-D2902 |  |  | HW |  |  | L | 300 | 150# RF |  | 0 ~ 80 | - | 3.5 |  | 45 | 40 |  |  | 16" | LC

## Process Data (hidden)
CLIENT |  |  |  | LG CHEM. | [13 empty] | REV. | DATE | EXEC. | CHEKED | APR'D | DESCRIPTION
PLANT/UNIT |  |  |  | IPA | [13 empty] | A | 2018-06-29 | J.R.M | M.K.L | G.J.K | AFD
LOCATION |  |  |  | YEOSU, KOREA
WORK NO
[9 empty] | Operating Condition |  |  |  | Design Condition |  |  |  | Liquid Flow |  |  | Vapor Flow
Rev |  | Tag No. | Q'ty | Service | Line |  | Fluid |  | Pressure |  | Temp |  | Pressure |  | Temp |  | Flow Rate | Density | Viscosity | Flow Rate | Density | Viscosity | P&I No. | REMARKS
[9 empty] | kg/cm2G |  | deg C |  | kg/cm2G |  | deg C
[5 empty] | Size | Spec. | Name | State | Normal | Max. | Normal | Max. | Normal | Max. | Hot | Cold | kg/h | kg/m3 | cp | kg/h | kg/m3 | cp
|  | Tag No. |  | Service | Size | Spec. | Fluid | State | oper. press. normal | oper. press. max | oper. temp. nomal | oper. temp. max | desi. press. normal | desi. press. max | desi. temp. Hot | desi. temp. Cold | Liquid Flow Flow Rate | Liquid Flow Density | Liquid Flow Viscosity | Vapor Flow Flow Rate | Vapor Flow Density | Vapor Flow Viscosity | P&I No. | REMARKS
A | TI | TI-1112A | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112B | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112C | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112D | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112E | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112F | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112G | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112H | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112I | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1112J | 1 | DC-110 EQUIPMENT | - | DC-110 | PRP | V | 40 |  | 208 |  | 55 |  | 280 | [7 empty] | D-1-IPA-1001
A | TI | TI-1118 | 1 | DC-110 INLET | 12" | BB59C1 | PRG | V | 40 |  | 192 |  | 55 |  | 280 |  |  |  |  | 134297 | 46.2233 | 0.015642 | D-1-IPA-1001 | INT.SPEC BREAK : FF59C
A | TI | TI-1119 | 1 | DC-110 INLET | 12" | BB59C1 | PRG | V | 40 |  | 192 |  | 55 |  | 280 |  |  |  |  | 134297 | 46.2233 | 0.015642 | D-1-IPA-1001
A | TI | TI-1121 | 1 | EA-110 TUBE INLET | 12" | BB59C1 | PRG | M | 40.4 |  | 172.1 |  | 55 |  | 280 |  | 3519.758 | 813.4887 | 0.15066 | 130777 | 51.8364 | 0.01517 | D-1-IPA-1001
A | TI | TI-1122 | 1 | DC-110 OUTLET | 12" | RD59V | PRP | V | 36.8 |  | 208 |  | 55 |  | 250 |  |  |  |  | 134297 | 41.3844 | 0.015779 | D-1-IPA-1001 | INT.SPEC BREAK : -
A | TI | TI-1123 | 1 | EA-111 SHELL INLET | 12" | BB59C1 | PRG | M | 42.7 |  | 148.8 |  | 55 |  | 250 |  | 10344 | 838.7 | 0.175 | 124492 | 66.87 | 0.015 | D-1-IPA-1001
A | TI | TI-1125 | 1 | EA-111 TUBE OUTLET | 10" | RD59V | PRP | M | 35.8 |  | 158.3 |  | 55 |  | 250 |  | 4300 | 826.5 | 0.164 | 130536 | 50.12 | 0.014 | D-1-IPA-1001 | INT.SPEC BREAK : -
A | TI | TI-1128 | 1 | EA-112 TUBE OUTLET | 10" | FF59C | PRP | V | 34.2 |  | 123.9 |  | 55 |  | 150 |  |  |  |  | 119558 | 82.5776 | 0.013622 | D-1-IPA-1001
A | TI | TI-1129 | 1 | FRESH PROPYLENE TO EA-112 SHELL SIDE | 4" | BB59C1 | PPF | L | 49.7 |  | 25 | 35 | 55 |  | 65 | -15 | 4524 | 507.168 | 0.080344 |  |  |  | D-1-IPA-1001
A | TI | TI-1133 | 1 | EA-112 SHELL INLET | 10" | BB59C1 | PRG | V | 44.8 |  | 120 |  | 55 |  | 180 |  |  |  |  | 119297 | 149.1764 | 0.016687 | D-1-IPA-1001
A | TI | TI-1134 | 1 | EA-112 TUBE OUTLET | 3" | FF59C | PDI | L | 33.1 |  | 40 |  | 55 |  | 250 |  | 14739.6761 | 828.0775 | 0.21654 |  |  |  | D-1-IPA-1001
A | TI | TG-1134 | 1 | FA-134 EQUIPMENT | - | FA-134 | PDI | L | HOLD |  | HOLD |  | HOLD |  | HOLD | [7 empty] | D-1-IPA-0004 | PH SAMPLE SYSTEM HOLD
A | TI | TI-1135 | 1 | GA-115A/B DISCHARGE | 3" | BB59C1 | PPW | L | 49.8 |  | 102.9 |  | 61.1 |  | 160 |  | 17568.9247 | 883.26 | 0.2716 |  |  |  | D-1-IPA-1001
A | TI | TI-1136 | 1 | PROCESS WATER TO EA-112 SHELL SIDE | 3" | BB59C1 | PPW | L | 49.5 |  | 102.9 |  | 61.1 |  | 160 |  | 17568.9247 | 883.26 | 0.2716 |  |  |  | D-1-IPA-1001
A | TG | TG-1140 | 1 | GB-120 DISCHARGE | 6" | BB59C1 | PRG | V | 47 |  | HOLD |  | 55 |  | 180 |  |  |  |  | 194001 | 90.0172 | 0.014233 | D-1-IPA-1002 | COMP. DISC. Temp. HOLD (by VENDOR)
A | TG | TG-1142 | 1 | GB-120 SUCTION | 12" | BB59C1 | PRG | V | 31 |  | 94 |  | 55 |  | 150 |  |  |  |  | 109401 | 66.3945 | 0.012709 | D-1-IPA-1002
A | TI | TI-1142 | 1 | GB-120 SUCTION | 12" | BB59C1 | PRG | V | 31 |  | 94 |  | 55 |  | 150 |  |  |  |  | 109401 | 66.3945 | 0.012709 | D-1-IPA-1002
A | TI | TI-1145 | 1 | WASH WATER TO DA-140 TOP INLET | 4" | BB59C1 | PWW | L | 39.34 |  | 95 |  | 48.11 |  | 150 |  | 31166.67 | 962.9918 | 0.29576 |  |  |  | D-1-IPA-1002
A | TI | TI-1150 | 1 | DA-140 OVHD OUTLET | 12" | BB59C1 | PRG | V | 31.2 |  | 94.2 |  | 55 |  | 150 |  |  |  |  | 109401 | 66.9115 | 0.012722 | D-1-IPA-1002
A | TI | TI-1151 | 1 | EA-140A/B TUBE OUTLET | 8" | BB55C | WCR | L | 5 |  | 32 |  | 7 |  | 50 |  | 260022 | 991.7 | 0.63 |  |  |  | D-1-IPA-1002
A | TI | TI-1152 | 1 | EA-140A SHELL OUTLET | 8" | FF59C | PRP | M | 33.85 |  | 93.2 |  | 55 |  | 150 |  | 18414 | 476.6 | 0.069 | 104766 | 66.93 | 0.013 | D-1-IPA-1002
A | TI | TI-1153 | 1 | EA-140B SHELL OUTLET | 8" | FF59C | PRP | M | 33.85 |  | 93.2 |  | 55 |  | 150 |  | 18414 | 476.6 | 0.069 | 104766 | 66.93 | 0.013 | D-1-IPA-1002
A | TI | TI-1154 | 1 | REACTION GAS TO DA-140 BTM. INLET | 10" | FF59C | PRP | M | 33.85 |  | 93.2 |  | 55 |  | 150 |  | 14239.5598 | 506.9992 | 0.068991 | 105318 | 62.6493 | 0.012821 | D-1-IPA-1002
A | TI | TI-1155 | 1 | REACTION GAS TO DA-140 BTM. INLET | 10" | FF59C | PRP | M | 33.85 |  | 93.2 |  | 55 |  | 150 |  | 14239.5598 | 506.9992 | 0.068991 | 105318 | 62.6493 | 0.012821 | D-1-IPA-1002
A | TI | TI-1157 | 1 | DA-140 BTM. OUTLET | 4" | BB59C1 | PDI | L | 31.6 |  | 94 |  | 55 |  | 150 |  | 56062.98 | 855.6228 | 0.28898 |  |  |  | D-1-IPA-1002
A | TI | TI-1158 | 1 | DA-140 1ST BED EQUIPMENT | - | DA-140 | PDI / PRG | M | 31.6 |  | 94 |  | 55 |  | 150 | [7 empty] | D-1-IPA-1002
A | TI | TI-1159 | 1 | DA-140 2ND BED EQUIPMENT | - | DA-140 | PDI / PRG | M | 31.6 |  | 94 |  | 55 |  | 150 | [7 empty] | D-1-IPA-1002
A | TG | TG-1158 | 1 | FC-150 OUTLWT | 4" | BB57C1 | PDI | L | 16.8 |  | 93 |  | 20 |  | 140 |  | 54185.3181 | 848.6701 | 0.25004 |  |  |  | D-1-IPA-1003
A | TG | TG-1159 | 1 | FC-155 OUTLET | 6" | BB55C1 | PDI | L | 0.4 |  | 82.4 |  | 2 |  | 120 |  | 52147.8999 | 890.2 | 0.349 |  |  |  | D-1-IPA-1003
A | TI | TI-1160 | 1 | FC-160 UNDER BED EQUIPMENT | - | FC-160 | PDI / PRG | M | 0.2 |  | 78 |  | 2 |  | 120 | [7 empty] | D-1-IPA-1003
A | TI | TI-1161 | 1 | FC-160 TOP EQUIPMENT | - | FC-160 | PRG | V | 0.1 |  | 54 |  | 2 |  | 120 | [7 empty] | D-1-IPA-1003
A | TG | TG-1162 | 1 | FC-160 BTM. OUTLET | 2" | BB55C1 | PDI | L | 0.69 |  | 77.7 |  | 2 |  | 120 |  | 1079.8878 | 739.1229 | 0.38061 |  |  |  | D-1-IPA-1003
A | TI | TI-1165 | 1 | EA-165 SHELL OUTLET | 4" | BB55C1 | PRG | M | 0.1 |  | 38 |  | 6 |  | 120 |  | 1244.9919 | 778.2831 | 0.84155 | 1118.5531 | 1.8983 | 0.0089599 | D-1-IPA-1003
A | TG | TG-1166 | 1 | WCR EA-165 TUBE OUTLET | 6" | BB55C | WCR | L | 2 |  | 42 |  | 7 |  | 50 |  | 51564.1 | 993.2 | 0.678 |  |  |  | D-1-IPA-1003
A | TI | TI-1168 | 1 | GB-170-1 SUCTION SNUBBER EQUIPMENT |  |  |  | V | [14 empty] | D-1-IPA-1003 | VENDOR SCOPE
A | TI | TI-1173 | 1 | GB-170-2 DISCHARGE SNUBBER EQUIPMENT |  |  |  | V | [14 empty] | D-1-IPA-1003 | VENDOR SCOPE
A | TI | TI-1174 | 1 | GB-170-2 DISCHARGE SNUBBER EQUIPMENT |  |  |  | V | [14 empty] | D-1-IPA-1003 | VENDOR SCOPE
A | TI | TI-1177 | 1 | EA-175X SHELL OUTLET | 3" | XXXXX | PRG | [15 empty] | D-1-IPA-1003 | VENDOR SCOPE
A | TI | TI-1210 | 1 | DA-210 BTM. EQUIPMENT | - | DA-210 | PHE | L | 16.5 |  | 175 |  | 25 |  | 200 | [7 empty] | D-1-IPA-2001
A | TI | TI-1211 | 1 | DA-210 UNDER 2ND BED EQUIPMENT | - | DA-210 | PHE | L | 16.5 |  | 175 |  | 25 |  | 200 | [7 empty] | D-1-IPA-2001
A | TI | TI-1212 | 1 | DA-210 2ND BED EQUIPMENT | - | DA-210 | PRG | M | 16.5 |  | 167.5 |  | 25 |  | 200 | [7 empty] | D-1-IPA-2001
A | TI | TI-1213 | 1 | DA-210 TOP EQUIPMENT | - | DA-210 | PRG | V | 16.5 |  | 41 |  | 25 |  | 200 | [7 empty] | D-1-IPA-2001
A | TI | TI-1215 | 1 | DA-210 OVHD OUTLET | 6" | BB57C1 | PRG | V | 16.5 |  | 41.2 |  | 25 |  | 120 |  |  |  |  | 7914.7915 | 36.8033 | 0.010176 | D-1-IPA-2001
A | TI | TI-1216 | 1 | DA-210 1ST BED EQUIPMENT | - | DA-210 | PRG | M | 16.5 |  | 42.8 |  | 25 |  | 200 | [7 empty] | D-1-IPA-2001
A | TI | TI-1217 | 1 | EA-215 SHELL OUTLET | 4" | BB57C1 | PPR | L | 16.4 |  | 39 |  | 25 |  | 120 |  | 7914.7915 | 453.2671 | 0.067598 |  |  |  | D-1-IPA-2001
A | TI | TI-1218 | 1 | EA-215 TUBESIDE COOLING WATER RETURN | 6" | BB55C | WCR | L | 4.3 |  | 36 |  | 7 |  | 50 |  | 145701 | 993.9 | 0.705 |  |  |  | D-1-IPA-2001
A | TI | TI-1219 | 1 | EA-217 VAPOR OUTLET | 1" | BB57C1 | PRG | V | 16.4 |  | 39 |  | 25 |  | 120 |  |  |  |  | 55 | 3.99 | 0.007 | D-1-IPA-2001
A | TI | TI-1220 | 1 | DA-220 BTM. EQUIPMENT | 1" | DA-220 | PHE | L | 19.6 |  | 52 |  | 25 |  | 120 | [7 empty] | D-1-IPA-2002
A | TI | TI-1221 | 1 | DA-220 3 STAGE EQUIPMENT | - | DA-220 | PHE / PPR | M | 19.6 |  | 52 |  | 25 |  | 120 | [7 empty] | D-1-IPA-2002
A | TI | TI-1223 | 1 | DA-220 TOP EQUIPMENT | - | DA-220 | PPR | V | 19.1 |  | 48 |  | 25 |  | 120 | [7 empty] | D-1-IPA-2002
A | TI | TI-1225 | 1 | WCR EA-225 TUBE OUTLET | 4" | BB55C | WCR | L | 4.3 |  | 42 |  | 7 |  | 50 |  | 44832.8 | 991.7 | 0.629 |  |  |  | D-1-IPA-2002
A | TI | TI-1226 | 1 | EA-225 SHELL OUTLET | 4" | BB57C1 | PPR | L | 19 |  | 47.4 |  | 25 |  | 120 |  | 6543.2619 | 465.3441 | 0.076447 |  |  |  | D-1-IPA-2002
A | TI | TI-1227 | 1 | FA-223 EQUIPMENT | - | FA-223 | PHE | L | 5.5 |  | 7 |  | 7.5 |  | 120 | [7 empty] | D-1-IPA-2002
A | TI | TI-1228 | 1 | DA-220 BTM. EQUIPMENT | 1" | DA-220 | PHE | L | 19.6 |  | 52 |  | 25 |  | 120 | [7 empty] | D-1-IPA-2002
A | TI | TI-1310 | 1 | DA-310 BTM. EQUIPMENT | - | DA-310 | PDI | L | 0.3 |  | 98 |  | 2 |  | 150 | [7 empty] | D-1-IPA-3001
A | TI | TI-1311 | 1 | DA-310 10 STAGE EQUIPMENT | - | DA-310 | PDI | M | 0.09 |  | 99 |  | 2 |  | 150 | [7 empty] | D-1-IPA-3001
A | TI | TI-1312 | 1 | WCR EA-316 TUBE OUTLET | 6" | BB55C | WCR | L | 4.3 |  | 42 |  | 7 |  | 50 |  | 82320.2 | 991.7 | 0.629 |  |  |  | D-1-IPA-3001
A | TI | TI-1313 | 1 | EA-316 SHELL OUTLET LIQUID | 2" | BB55C1 | PDI | L | 0.04 |  | 45 |  | 6 |  | 150 |  | 1792 | 895 | 0.577 |  |  |  | D-1-IPA-3001
A | TI | TI-1314 | 1 | DA-310 OVHD OUTLET | 8" | BB55C1 | PDI | V | 0.05 |  | 94 |  | 6 |  | 150 |  |  |  |  | 1792 | 0.9777 | 0.012241 | D-1-IPA-3001
A | TI | TI-1315 | 1 | GA-315A/B DISCHARGE | 3" | BB55C1 | PDI | L | 0.1 |  | 98 |  | 7.38 |  | 150 |  | 2767.7644 | 969.38 | 0.611 |  |  |  | D-1-IPA-3001
A | TI | TI-1316 | 1 | DA-310 3 STAGE EQUIPMENT | - | DA-310 | PDI | M | 0.24 |  | 95.7 |  | 2 |  | 150 | [7 empty] | D-1-IPA-3001
A | TI | TI-1317 | 1 | EA-316 SHELL OUTLET VAPOR | 2" | BB55C1 | PDI | V | 0.04 |  | 45 |  | 6 |  | 150 |  |  |  |  | 1792 | 895 | 0.577 | D-1-IPA-3001
A | TI | TI-1318 | 1 | EA-317 SHELL OUTLET TO FLARE | 2" | BB55C | VA | V | 0 |  | 45 |  | 2 |  | 150 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-3001
A | TI | TI-1319 | 1 | WCR EA-317 TUBE OUTLET | 1 1/2" | BB55C | WCR | L | 4.3 |  | 42 |  | 7 |  | 50 |  | HOLD | 991.7 | 0.629 |  |  |  | D-1-IPA-3001
A | TI | TI-1320 | 1 | DA-320 BTM. EQUIPMENT | - | DA-320 | PWW | L | 2 |  | 133 |  | 4 |  | 180 | [7 empty] | D-1-IPA-3002
A | TI | TI-1321 | 1 | DA-320 AVOBE 3 STAGE EQUIPMENT | - | DA-320 | PWW | L | 2 |  | 133 |  | 4 |  | 180 | [7 empty] | D-1-IPA-3002
A | TI | TI-1329 | 1 | DA-320 17 - 16 STAGE EQUIPMENT | - | DA-320 | PDI | V | 1.92 |  | 122.3 |  | 4 |  | 180 | [7 empty] | D-1-IPA-3002
A | TI | TI-1322 | 1 | DA-320 17 - 16 STAGE EQUIPMENT | - | DA-320 | PDI | V | 1.92 |  | 122.3 |  | 4 |  | 180 | [7 empty] | D-1-IPA-3002
A | TI | TI-1323 | 1 | DA-320 19 - 18 STAGE EQUIPMENT | - | DA-320 | PDI | V | 1.91 |  | 112.2 |  | 4 |  | 180 | [7 empty] | D-1-IPA-3002
A | TI | TI-1324 | 1 | DA-320 20 - 19 STAGE EQUIPMENT | - | DA-320 | PDI | V | 1.9 |  | 111 |  | 4 |  | 180 | [7 empty] | D-1-IPA-3002
A | TI | TI-1325 | 1 | DA-320 22 - 21 STAGE EQUIPMENT | - | DA-320 | PDI | V | 1.89 |  | 110.3 |  | 4 |  | 180 | [7 empty] | D-1-IPA-3002
A | TI | TI-1326 | 1 | DA-320 OVHD OUTLET | 12" | BB55C1 | PDI | V | 1.6 |  | 106 |  | 4 |  | 180 |  |  |  |  | 21211.67 | 3.9822 | 0.011038 | D-1-IPA-3002
A | TI | TI-1327 | 1 | EA-320A/B/C TUBE OUTLET | 6" | BB55C1 | PDI | L | 3.6 |  | 122 |  | 8 |  | 180 |  | 99457 | 875.9 | 0.225 |  |  |  | D-1-IPA-3002
A | TG | TG-1328 | 1 | EA-320A/B/C SHELL OUTLET | 8" | BB55C1 | PWW | L | 5.65 |  | 106.9 |  | 10 |  | 180 |  | 91358 | 910.9 | 0.26 |  |  |  | D-1-IPA-3002
A | TI | TI-1330 | 1 | DA-330 UNDER 4TH BED | - | DA-330 | PDI | L | 2.05 |  | 115.8 |  | 4 |  | 160 | [7 empty] | D-1-IPA-3002
A | TI | TI-1331 | 1 | DA-330 3 - 4 BED EQUIPMENT | - | DA-330 | PDI | M | 2 |  | 112 |  | 4 |  | 160 | [7 empty] | D-1-IPA-3002
A | TI | TI-1332 | 1 | DA-330 2 - 3 BED EQUIPMENT | - | DA-330 | PDI | M | 1.97 |  | 111.6 |  | 4 |  | 160 | [7 empty] | D-1-IPA-3002
A | TI | TI-1333 | 1 | DA-330 1 - 2 BED EQUIPMENT | - | DA-330 | PDI | M | 1.93 |  | 111 |  | 4 |  | 160 | [7 empty] | D-1-IPA-3002
A | TI | TI-1335 | 1 | DA-330 OVHD OUTLET | 6" | BB55C1 | PDI | V | 1.9 |  | 111 |  | 4 |  | 160 |  |  |  |  | 3543.75 | 3.83 | 0.011662 | D-1-IPA-3002
A | TG | TG-1336 | 1 | EA-333 OUTLET TO WWT | 1" | BB55C1 | PDI | L | 1.95 |  | 40 |  | 6 |  | 160 |  | 945 | 890.8 | 0.771 |  |  |  | D-1-IPA-3002
A | TI | TI-1337 | 1 | DA-320 AVOBE 5 STAGE EQUIPMENT | - | DA-320 | PWW | L | 2 |  | 133 |  | 4 |  | 180 | [7 empty] | D-1-IPA-3002
A | TI | TI-1340 | 1 | DA-340 2ND BED EQUIPMENT | - | DA-340 | PDI | V | 0.03 |  | 81 |  | 2 |  | 150 | [7 empty] | D-1-IPA-3003
A | TI | TI-1341 | 1 | DA-340 2 - 3 BED EQUIPMENT | - | DA-340 | PDI | V | 0.07 |  | 81.7 |  | 2 |  | 150 | [7 empty] | D-1-IPA-3003
A | TI | TI-1344 | 1 | DA-340 TOP EQUIPMENT VENNT TO FLARE | 3" | BB55C | WCS | L | 5 |  | 32 |  | 7 |  | 50 |  | 24253 | 995.3 | 0.764 |  |  |  | D-1-IPA-3003
A | TI | TI-1345 | 1 | EA-345 SHELL SIDE EQUIPMENT | - | EA-345 | PDI | V | 0.02 |  | 56 |  | 2 |  | 150 | [7 empty] | D-1-IPA-3003
A | TI | TI-1346 | 1 | EA-325 SHELL INLET | 12" | BB55C1 | PDI | M | 1.5 |  | 105 |  | 6 |  | 180 |  | 15225 | 715.2 | 0.298 | 5237 | 3.84 | 0.011 | D-1-IPA-3003
A | TI | TI-1347 | 1 | WCR EA-325 TUBE OUTLET | 8" | BB55C | WCR | L | 5 |  | 42 |  | 7 |  | 50 |  | 194235 | 995.3 | 0.764 |  |  |  | D-1-IPA-3003
A | TI | TI-1348 | 1 | EA-325 SHELL OUTLET | 6" | BB55C1 | PDI | L | 1.5 |  | 50 |  | 6 |  | 150 |  | 20462 | 787.4 | 0.852 |  |  |  | D-1-IPA-3003
A | TI | TI-1381 | 1 | EA-327 SHELL SIDE VENT TO FLARE | 2" | BB55C | VA | V | 0.01 |  | 40 |  | 6 |  | 150 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-3003
A | TI | TI-1382 | 1 | WCR EA-327 TUBE OUTLET | 1" | BB55C | WCR | L | 5 |  | 42 |  | 7 |  | 50 |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-3003
A | TI | TI-1383 | 1 | EA-327 SHELL OUTLET | 1" | BB55C1 | PDI | L | 0.01 |  | 40 |  | 6 |  | 150 |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-3003
A | TI | TI-1384 | 1 | EA-324 TUBE OUTLET | 3" | BB55C1 | WW | L | 4.3 |  | 40 |  | 8 |  | 150 |  | 17764 | 920.5 | 0.286 |  |  |  | D-1-IPA-3003
A | TI | TI-1385 | 1 | WCR EA-324 SHELL OUTLET | 6" | BB55C | WCR | L | 2 |  | 40 |  | 7 |  | 50 |  | 132225 | 992.5 | 0.655 |  |  |  | D-1-IPA-3003
A | TI | TI-1386 | 1 | WASH WATER EA-323 TUBE OUTLET | 6" | BB55C1 | PWW | L | 5 |  | 97.9 |  | 8 |  | 150 |  | 91358 | 920.5 | 0.286 |  |  |  | D-1-IPA-3003
A | TI | TI-1387 | 1 | DEMI WATER EA-323A/B SHELL OUTLET | 3" | BB55C1 | WT | L | 5.7 |  | 75.9 |  | 10 |  | 160 |  | 15746 | 974.6 | 0.374 |  |  |  | D-1-IPA-3003
A | TI | TI-1388 | 1 | DEMI WATER TO EA-323A/B INLET | 3" | BB55C1 | WT | L | 6 |  | 20 |  | 10 |  | 150 |  | HOLD | 998.5 | 1.0014 |  |  |  | D-1-IPA-8013
A | TI | TI-1389 | 1 | WASH WATER TO DA-310 | 4" | BB55C1 | PWW | L | 5 |  | 97.9 |  | 8 |  | 150 |  | 31635 | 960.1 | 0.2861 |  |  |  | D-1-IPA-3003
A | TI | TI-1390 | 1 | WASH WATER TO DA-310 | 4" | BB55C1 | PWW | L | 5 |  | 97.9 |  | 8 |  | 150 |  | 46287 | 960.1 | 0.2861 |  |  |  | D-1-IPA-3003
A | TI | TI-1391 | 1 | DEMI WATER TO EA-812 | 3" | BB55C1 | PWW | L | 5.7 |  | 75.9 |  | 10 |  | 160 |  | 20462 | 974.6 | 0.374 |  |  |  | D-1-IPA-3003
A | TI | TI-1350 | 1 | DA-350 BTM. EQUIPMENT | - | DA-350 | PIP | L | 0.4 |  | 90 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1351A | 1 | EA-351A SHELL OUTLET | 3" | BB55C1 | PDI | L | 1.6 |  | 104.4 |  | 4 |  | 150 |  | 20462 | 715.2 | 0.298 |  |  |  | D-1-IPA-3004
A | TI | TI-1351B | 1 | EA-351B SHELL OUTLET | 3" | BB55C1 | PDI | L | 1.6 |  | 104.4 |  | 4 |  | 150 |  | 20462 | 715.2 | 0.298 |  |  |  | D-1-IPA-3004
A | TI | TI-1352 | 1 | DA-350 17 - 15 STAGE EQUIPMENT | - | DA-350 | PIP | M | 0.28 |  | 88 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1353 | 1 | EA-353A/B SHELL OUTLET | 2" | BB55C1 | PIP | L | 0.003 |  | 40 |  | 6 |  | 120 |  | 6271.058 | 774.837 | 1.3404 |  |  |  | D-1-IPA-3004
A | TI | TI-1354 | 1 | FA-354 EQUIPMENT | - | FA-354 | PS | L | 0 |  | 30 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1355 | 1 | WCR EA-353A/B TUBE OUTLET | 4" | BB55C | WCR | L | 2 |  | 42 |  | 7 |  | 50 |  | 30594 | 992.4 | 0.653 |  |  |  | D-1-IPA-3004
A | TI | TI-1356 | 1 | DA-350 61 - 59 STAGE EQUIPMENT | - | DA-350 | PIP | M | 0.06 |  | 60.5 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1357 | 1 | DA-350 OVHD OUTLET | 16" | BB55C1 | PDI | V | 0.1 |  | 75 |  | 2 |  | 120 |  |  |  |  | 27776.19 | 2.4109 | 0.0090684 | D-1-IPA-3004
A | TI | TI-1359 | 1 | DA-350 22 - 19 STAGE EQUIPMENT | - | DA-350 | PIP | M | 0.26 |  | 87.5 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1360 | 1 | DA-350 37 STAGE EQUIPMENT | - | DA-350 | PIP | M | 0.17 |  | 82.6 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1361 | 1 | DA-350 24 STAGE EQUIPMENT | - | DA-350 | PIP | M | 0.24 |  | 87 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1362 | 1 | DA-350 12 STAGE EQUIPMENT | - | DA-350 | PIP | M | 0.28 |  | 88.5 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1363 | 1 | DA-350 4 STAGE EQUIPMENT | - | DA-350 | PIP | M | 0.34 |  | 89.3 |  | 2 |  | 120 | [7 empty] | D-1-IPA-3004
A | TI | TI-1395A | 1 | EA-355 SHELL OUTLET | 6" | BB55C1 | PDI | L | 0.003 |  | 40 |  | 6 |  | 120 |  | 27776 | 800.1 | 0.773 |  |  |  | D-1-IPA-3005
A | TI | TI-1396A | 1 | WCR EA-355 TUBE OUTLET | 10" | BB55C | WCR | L | 2 |  | 40 |  | 7 |  | 50 |  | 508243 | 992.4 | 0.653 |  |  |  | D-1-IPA-3005
A | TI | TI-1397 | 1 | EA-357 SHELL OUTLET | 2" | BB55C1 | PDI | L | 0.003 |  | 40 |  | 6 |  | 120 |  | 200 | HOLD | HOLD |  |  |  | D-1-IPA-3005
A | TI | TI-1398 | 1 | EA-357 SHELL OUTLET VENT TO FLARE | 2" | BB55C | GFL | V | 0.003 |  | 40 |  | 6 |  | 120 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-3005
A | TI | TI-1399 | 1 | WCR EA-357 TUBE OUTLET | 1 1/2" | BB55C | WCR | L | 2 |  | 42 |  | 7 |  | 50 |  | 5000 | 991.7 | 0.629 |  |  |  | D-1-IPA-3005
A | TI | TI-13600 | 1 | DA-360 BTM EQUIPMENT | - | DA-360 | PPW | L | 0.3 |  | 108 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-13601 | 1 | DA-360 AVOBE 17 STAGE EQUIPMENT | - | DA-360 | PDI | V | 0.25 |  | 97.8 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-13602 | 1 | DA-360 MIDDLE EQUIPMENT | - | DA-360 | PDI | V | 0.19 |  | 96.5 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-13603 | 1 | DA-360 UNDER 13 STAGE EQUIPMENT | - | DA-360 | PDI | V | 0.27 |  | 106.6 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-13604 | 1 | DA-360 TOP EQUIPMENT | - | DA-360 | PDI | V | 0.06 |  | 80 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-13605 | 1 | DA-360 AVOBE 3 STAGE EQUIPMENT | - | DA-360 | PPW | L | 0.32 |  | 107.8 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-13606 | 1 | DA-360 52 - 50 STAGE EQUIPMENT | - | DA-360 | PDI | V | 0.08 |  | 94.1 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-13607 | 1 | DA-360 54 - 52 STAGE EQUIPMENT | - | DA-360 | PDI | V | 0.07 |  | 93.8 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-13608 | 1 | DA-360 56 - 54 STAGE EQUIPMENT | - | DA-360 | PDI | V | 0.06 |  | 91.1 |  | 2 |  | 140 | [7 empty] | D-1-IPA-3006
A | TI | TI-1366 | 1 | DA-360 OVHD OUTLET | 12" | BB55C1 | PDI | V | 0.1 |  | 80.3 |  | 2 |  | 140 |  | 1298.915 | 1.5874 | 0.010427 |  |  |  | D-1-IPA-3006
A | TI | TI-1367 | 1 | EA-365 GAS SHELL OUTLET | 2" | BB55C1 | PDI | V | 0.04 |  | 73.7 |  | 6 |  | 120 |  |  |  |  | HOLD | 1.59 | 0..01 | D-1-IPA-3006
A | TI | TI-1368 | 1 | EA-365 LIQUID SHELL OUTLET | 2" | BB55C1 | PDI | L | 0.04 |  | 73.7 |  | 6 |  | 120 |  | 1298.915 | 764.9887 | 0.45934 |  |  |  | D-1-IPA-3006
A | TI | TI-1369 | 1 | WCR EA-365 TUBE OUTLET | 6" | BB55C | WCR | L | 2 |  | 42 |  | 7 |  | 50 |  | 28818 | 991.7 | 0.629 |  |  |  | D-1-IPA-3006
A | TI | TI-1375 | 1 | PURE IPA TO DT-420A/B | 4" | BB55C1 | PIP | L | 4.66 |  | 40 |  | 6.05 |  | 120 |  | 38740 | 774.8 | 1.34 |  |  |  | D-1-IPA-3007
A | TG | TI-1410(1401) | 1 | PROPYLENE FROM GA-410A/B | 2" | BB57C1 | PPR | L | 18 |  | 25 | 35 | 30.1 |  | 65 |  | 6000 | 504.4 | 0.09 |  |  |  | D-1-IPA-4001
A | TI | TG-1401 | 1 | PROPYLENE FROM GA-410A/B | 2" | BB57C1 | PPR | L | 18 |  | 25 | 35 | 30.1 |  | 65 |  | 6000 | 504.4 | 0.09 |  |  |  | D-1-IPA-4001
A | TI | TI-1410 | 1 | FA-415 EQUIPMENT | - | FA-415 | PPR | L | 15.2 |  | AMB |  | 25 |  | 65 | -15 | [6 empty] | D-1-IPA-4001
A | TI | TI-1411 | 1 | FA-415 BTM. OUTLET | 4" | BB57C1 | PPR | L | 15.2 | 18.89 | 25 | 35 | 25 | - | 65 | -15 | 2114 | 486 | 0.0803 |  |  |  | D-1-IPA-4001
A | TI | TI-1415 | 1 | FA-415 BTM. OUTLET | 4" | BB57C1 | PPF | L | 15.39 | 18.89 | 25 | 35 | 25 |  | 65 | -15 | 7057 | 507.2 | 0.08 |  |  |  | D-1-IPA-4001
A | TI | TI-1420A | 1 | FB-420A EQUIPMENT | - | FB-420A | PIP | L | 0 |  | 40 |  | 0.01 / -0.0075 |  | 120 | [7 empty] | D-1-IPA-4002
A | TI | TI-1420B | 1 | FB-420B EQUIPMENT | - | FB-420B | PIP | L | 0 |  | 40 |  | 0.01 / -0.0075 |  | 120 | [7 empty] | D-1-IPA-4002
A | TI | TI-1801 | 1 | BG-801 OUTLET | 6" | BA59C | HS | S | 40 |  | 370 |  | 45 / FV |  | 425 |  | 22160 | 15.481 | 0.02 |  |  |  | D-1-IPA-8011
A | TI | TI-1802 | 1 | B.F.W FROM B.L | 1.1/2" | HOLD | BFW | L | 64.6 |  | 80 |  | HOLD |  | HOLD | [7 empty] | D-1-IPA-8011
A | TI | TI-1805 | 1 | MSS TO BG-803 | 10" | BB57C | MSS | S | 14.6 |  | 226 |  | HOLD |  | HOLD |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8011
A | TI | TI-1807 | 1 | MSS TO BG-803 | 10" | BB57C | MSS | S | HOLD |  | HOLD |  | HOLD |  | HOLD |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8011
A | TI | TI-1811 | 1 | BG-801 OUTLET | 4" | BA59C | SH | S | 31 |  | 255 |  | 46 / FV |  | 400 |  | 6123 | 14.7 | 0.0179 |  |  |  | D-1-IPA-8011
A | TI | TI-1812 | 1 | BG-802 OUTLET | 10" | BB57C | SM | S | 9.8 |  | 198 |  | 12 / FV |  | 250 |  | 15530 | 5.208 | 0.015 |  |  |  | D-1-IPA-8011
A | TI | TI-1813 | 1 | DEMI WATER EA-812 SHELL OUTLET | 3" | BB55C1 | WT | L | HOLD |  | HOLD |  | HOLD |  | HOLD | [7 empty] | D-1-IPA-8011
A | TI | TI-1814 | 1 | LOW PRESSURE STEAM TO CONSUMER | X" | BB55C | SL | S | HOLD |  | HOLD |  | HOLD |  | HOLD | [7 empty] | D-1-IPA-8011
A | TI | TI-1815 | 1 | EA-815 SHELL OUTLET VENT TO ATM. | 2" | BB55C | VA | V | HOLD |  | HOLD |  | HOLD |  | HOLD | [7 empty] | D-1-IPA-8011
A | TI | TI-1816 | 1 | WCR EA-815 TUBE OUTLET | 4" | BB55C | WCR | L | HOLD |  | HOLD |  | HOLD |  | HOLD | [7 empty] | D-1-IPA-8011
A | TI | TI-1818 | 1 | CL TO BG-802, BG-803 | 1 1/2" | BB55C | LC | L | HOLD |  | HOLD |  | HOLD |  | HOLD | [7 empty] | D-1-IPA-8011
A | TI | TI-1820 | 1 | CWS GA-820A/B DISCHARGE | 18" | BB55C | WCS | L | HOLD |  | HOLD |  | HOLD |  | HOLD |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8012
A | TI | TI-1821 | 1 | CWR EF-820 INLET | 18" | BB55C | WCR | L | 2 |  | 42 |  | 7 |  | 50 |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8012
A | TI | TI-1830 | 1 | FA-830X EQUIPMENT | - | FA-830X | WT | L | HOLD |  | HOLD |  | HOLD |  | HOLD |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8013 | DEAERATOR HOLD
A | TI | TI-1839 | 1 | POLISHED WATER FROM B.L | 3" | BB55C1 | WT | L | 5 |  | AMB |  | 7 |  | AMB |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8013
A | TI | TI-1842 | 1 | INSTRUMENT AIR FROM BL | 4" | BC55C | AI | V | 7 |  | AMB |  | 9 |  | 60 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8014
A | TI | TI-1847 | 1 | LOW PRESSURE NITROGEN FROM BL | 3" | BB55C | NL | V | 7 |  | AMB |  | 9 |  | 60 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8014
A | TI | TI-1860 | 1 | FA-860 EQUIPMENT | - | FA-860 | PDI | L | 0.3 |  | AMB |  | 2 |  | 300 |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8023
A | TI | TI-1870 | 1 | PLNAT AIR FROM BL | 3" | BC55C | AP | V | 7 |  | AMB |  | 9 |  | 60 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8015
A | TI | TI-1880 | 1 | FILTERED WATER FROM B.L | 4" | BB55C | WR | L | 4 |  | AMB |  | 7 |  | 60 |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8022
A | TI | TI-1890 | 1 | WASTE WATER FROM EA-324 | 3" | BB55C1 | WW | L | 4.19 |  | 40 |  | 8 |  | 150 |  | 13857.8 | 992.5 | 0.653 |  |  |  | D-1-IPA-8024
A | TG | TG-1420A | 1 | FB-420A EQUIPMENT | - | FB-420A | PIP | L | 0 |  | 40 |  | 0.01 / -0.0075 |  | 120 | [7 empty] | D-1-IPA-4002
A | TG | TG-1420B | 1 | FB-420B EQUIPMENT | - | FB-420B | PIP | L | 0 |  | 40 |  | 0.01 / -0.0075 |  | 120 | [7 empty] | D-1-IPA-4002
A | TG | TG-1801 | 1 | BG-801 OUTLET | 6" | BA59C | HS | S | 40 |  | 370 |  | 45 / FV |  | 425 |  | 22160 | 15.481 | 0.02 |  |  |  | D-1-IPA-8011
A | TG | TG-1802 | 1 | B.F.W FROM B.L | 1.1/2" | HOLD | BFW | L | 64.6 |  | 80 |  | HOLD |  | HOLD | [7 empty] | D-1-IPA-8011
A | TG | TG-1820 | 1 | CWS GA-820A/B DISCHARGE | 18" | BB55C | WCS | L | HOLD |  | HOLD |  | HOLD |  | HOLD |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8012
A | TG | TG-1821 | 1 | CWR EF-820 INLET | 18" | BB55C | WCR | L | 2 |  | 42 |  | 7 |  | 50 |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8012
A | TG | TG-1830 | 1 | FA-830X EQUIPMENT | - | FA-830X | WT | L | HOLD |  | HOLD |  | HOLD |  | HOLD |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8013 | DEAERATOR HOLD
A | TG | TG-1831 | 1 | EA-830X SHELL SIDE EQUIPMENT | - | EA-830X | WT | L | HOLD |  | HOLD |  | HOLD |  | HOLD |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8013 | DEAERATOR HOLD
A | TG | TG-1805 | 1 | MSS TO BG-803 | 10" | BB57C | MSS | S | 14.6 |  | 226 |  | HOLD |  | HOLD |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8011
A | TG | TG-1833 | 1 | SM STEAM TO EA-830X TUBE INLET | 4" | BB57C | CM | L | HOLD |  | HOLD |  | HOLD |  | HOLD |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8013
A | TG | TG-1834 | 1 | CM CONDENSATE EA-830X TUBE OUTLET | 1 1/2" | BB57C | CM | L | HOLD |  | HOLD |  | HOLD |  | HOLD |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8013
A | TG | TG-1842 | 1 | INSTRUMENT AIR FROM BL | 4" | BC55C | AI | V | 7 |  | AMB |  | 9 |  | 60 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8014
A | TG | TG-1847 | 1 | LOW PRESSURE NITROGEN FROM BL | 3" | BB55C | NL | V | 7 |  | AMB |  | 9 |  | 60 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8014
A | TG | TG-1870 | 1 | PLNAT AIR FROM BL | 3" | BC55C | AP | V | 7 |  | AMB |  | 9 |  | 60 |  |  |  |  | HOLD | HOLD | HOLD | D-1-IPA-8015
A | TG | TG-1880 | 1 | FILTERED WATER FROM B.L | 4" | BB55C | WR | L | 4 |  | AMB |  | 7 |  | 60 |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8022
A | TG | TG-1860 | 1 | FA-860 EQUIPMENT | - | FA-860 | PDI | L | 0.3 |  | AMB |  | 2 |  | 300 |  | HOLD | HOLD | HOLD |  |  |  | D-1-IPA-8023
: HOLD (To be confirmed during Detail Engineering)
INSTRUMENT PROCESS DATA FOR TEMPERATURE
Note on N32: USER: Design Press. HOLD
Note on N33: USER: Design Press. HOLD
Note on J160: USER: 18.06.08 수정 5/31일 Steam Balance 참고
Note on L160: USER: 18.06.08 수정 5/31일 Steam Balance 참고
Note on J183: USER: 18.06.08 수정 5/31일 Steam Balance 참고
Note on L183: USER: 18.06.08 수정 5/31일 Steam Balance 참고