## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | GAS DETECTOR | [5 empty] | DS-IN-F-029
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
GAS DETECTOR
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | AUG.30.'18 |  |  | FOR QUOTAION |  | J.H Jung |  | C.M Lee | K.Y Noh |  |  | H.D Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-029 |  |  | 2018.08.30

## Gas Detector
|  |  |  | DATA SHEET | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  | : M0556 | GAS DETECTOR | DS-IN-F-029
| PROJECT NAME |  | : IPA 50KTA Exp. |  | REV. NO.
| LOCATION |  | : Yeosu, Korea |  | A
1 | GENERAL | Tag No. |  | See List
2 |  | Location |  | See List
3 |  | Detection Gas |  | See List
4 |  | Enclosure Class |  | Ex d IIB T4, IP56
5
6 | DETECTOR | Sensor Type |  | Diffusion
7 |  | Function |  | Smart Transmitter
8 |  | Indicator |  | Yes (LCD)
9 |  | Detectable Gas |  | Combustible Gas
10 |  | Measuring Method |  | Catalytic Cell
11 |  | Measuring Range |  | 0 ~ 100 % LEL
12 |  | High Alarm |  | 25 % LEL
13 |  | High High Alarm |  | 50 % LEL
14 |  | Response Time (90% of F.S) |  | ≤30 secs
15 |  | Accuracy |  | ± 3% / F.S
16 |  | Measuring Signal Output |  | 4~20 mA DC, HART
17 |  | Conduit Connection |  | 1/2" NPT(F)
18 |  | Signal Cable Connection |  | CVV-AMS 1.5 SQ. X 1T
19 |  | Mounting Type |  | 2" Pipe Mounting
20 |  | Power Supply |  | 24 VDC
21
22
23 | MONITORING SYSTEM | Type
24 |  | Analog I/O Unit
25 |  | Power Supply
26 |  | Input Signal
27 |  | Output Signal
28 |  | Alarm Signal
29 |  | Measuring Value Display
30 |  | Reset & Ark. Button
31 |  | Comunication Protocol
32 |  | Location
33 |  | Cabinet
34
35 | ACCESSORIES | Adapter For Calibration |  | Yes
36 |  | Calibration Gas |  | Yes
37 |  | Calibration Tool |  | Yes
38 |  | Mounting Bracket |  | Yes
39 |  | Weather Proof Cover |  | Yes
40 |  | Magnetic Stick |  | Yes
41
42 | PROQ. | Manufacturer
43 |  | Model
44
NOTE

## Item List
|  |  |  | DATA SHEET |  |  |  | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  | : M0556 | GAS DETECTOR |  |  |  | DS-IN-F-029
| PROJECT NAME |  | : IPA 50KTA Exp. |  |  |  |  | REV. NO.
| LOCATION |  | : Yeosu, Korea |  |  |  |  | A
No. | Tag No. | Detection Gas |  | Location | Range |  |  | Remark
[5 empty] | Alarm(1st) | Alarm(2nd) | Range
1 | GD-1101 | 프로필렌 |  | FA-121 | 25% | 50% | 0~100%
2 | GD-1102 | 프로필렌 |  | GB-170 | 25% | 50% | 0~100%
3 | GD-1103 | 프로필렌 |  | GB-170 | 25% | 50% | 0~100%
4 | GD-1104 | 프로필렌 |  | FC-150 | 25% | 50% | 0~100%
5 | GD-1105 | 프로필렌 |  | GB-120 | 25% | 50% | 0~100%
6 | GD-1106 | 프로필렌 |  | GB-120 | 25% | 50% | 0~100%
7 | GD-1107 | IPA |  | GA-155A/B | 25% | 50% | 0~100%
8 | GD-1201 | 프로필렌 |  | GA-225A/B | 25% | 50% | 0~100%
9 | GD-1301 | IPA |  | GA-313A/B | 25% | 50% | 0~100%
10 | GD-1302 | IPA |  | DA-320 | 25% | 50% | 0~100%
11 | GD-1303 | 사이클로헥산 |  | GA-431 | 25% | 50% | 0~100%
12 | GD-1304 | IPA |  | FA-325 | 25% | 50% | 0~100%
13 | GD-1305 | IPA |  | FA-374 | 25% | 50% | 0~100%
14 | GD-1306 | 사이클로헥산 |  | GA-355A GA-356A | 25% | 50% | 0~100%
15 | GD-1307 | IPA |  | GA-353A GA-353B | 25% | 50% | 0~100%
16 | GD-1308 | IPA |  | FA-373B/C | 25% | 50% | 0~100%
17 | GD-1309 | IPA |  | FA-371A FA-373A | 25% | 50% | 0~100%
18 | GD-1310 | IPA |  | GA-373A/B GA-371A/B | 25% | 50% | 0~100%
19 | GD-1311 | IPA |  | GA-365A GA-365B | 25% | 50% | 0~100%
20 | GD-1401 | 프로필렌 |  | FA-415 | 25% | 50% | 0~100%
21 | GD-1402 | 프로필렌 |  | GA-415A/B | 25% | 50% | 0~100%
22 | GD-1781 | IPE Oil |  | FA-781A | 25% | 50% | 0~100%
23 | GD-1782 | IPE Oil |  | FA-781A | 25% | 50% | 0~100%
24 | GD-1783 | IPE Oil |  | FA-781B | 25% | 50% | 0~100%
25 | GD-1784 | IPE Oil |  | GA-781A/B | 25% | 50% | 0~100%
26 | GD-1420 | IPA |  | FB-420A/B | 25% | 50% | 0~100%
27 | GD-1421 | IPA |  | FB-420A/B | 25% | 50% | 0~100%
28 | GD-1422 | IPA |  | FB-420A/B | 25% | 50% | 0~100%
29 | GD-1423 | IPA |  | GA-420A/B | 25% | 50% | 0~100%
30 | GD-1801 | HC |  | EF-820 상단 | 25% | 50% | 0~100%
31 | GD-1802 | HC |  | MCC Room | 25% | 50% | 0~100%
32 | GD-1803 | HC |  | GA-880A/B | 25% | 50% | 0~100%
33 | GD-1804 | 수소 |  | MCC Room B/C | 25% | 50% | 0~100% | 벽면 혹은 천정 설치
34 | GD-1805 | HC |  | 최종방류구(우수집수조) | 25% | 50% | 0~100%
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
NOTE