## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | CONTROL VALVE | [5 empty] | DS-IN-F-030
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
CONTROL VALVE
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | MAY.23.'17 |  |  | FOR QUOTAION |  | J.H Jung |  | C.M Lee | K.Y Noh |  |  | H.D Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-030 |  |  | 2018.05.23

## Control Valve
[5 empty] | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  | DATA SHEET | [12 empty] | CLIENT |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [11 empty] | CLIENT |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [10 empty] | CLIENT |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT |  |  | DATA SHEET | [12 empty] | CLIENT |  |  |  | DATA SHEET | [12 empty] | CLIENT
[18 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [15 empty] | LG Chem | [15 empty] | LG Chem | [16 empty] | LG Chem | [14 empty] | LG Chem | [15 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [16 empty] | LG Chem | [15 empty] | LG Chem | [16 empty] | LG Chem
[18 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [15 empty] | DOC. NO. | [15 empty] | DOC. NO. | [16 empty] | DOC. NO. | [14 empty] | DOC. NO. | [15 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [16 empty] | DOC. NO. | [15 empty] | DOC. NO. | [16 empty] | DOC. NO.
| JOB NO. |  | : M0556 |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [11 empty] | DS-IN-F-030 |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [10 empty] | DS-IN-F-030 |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030 |  |  |  | CONTROL VALVE (GLOBE) | [12 empty] | DS-IN-F-030
| PROJECT NAME |  | : IPA 50KTA Exp. | [14 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [15 empty] | REV. NO. | [15 empty] | REV. NO. | [16 empty] | REV. NO. | [14 empty] | REV. NO. | [15 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [16 empty] | REV. NO. | [15 empty] | REV. NO. | [16 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [14 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [15 empty] | A | [15 empty] | A | [16 empty] | A | [16 empty] | A | [15 empty] | A | [15 empty] | A | [16 empty] | A | [14 empty] | A | [15 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [16 empty] | A | [15 empty] | A | [16 empty] | A
1 | GENERAL | Tag No. |  |  | FV-1129 |  |  |  |  | FV-1136 |  |  |  | FV-1143 |  |  |  | FV-1145 |  |  |  | FV-1211 |  |  |  |  | FV-1212 |  |  |  | FV-1213 |  |  |  | FV-1221 |  |  |  | FV-1225 |  |  |  |  | FV-1226 |  |  |  | FV-1227 |  |  |  | FV-1311 |  |  |  | FV-1312 |  |  |  |  | FV-1314 |  |  |  | FV-1315 |  |  |  | FV-1316 |  |  |  | FV-1319 |  |  |  |  | FV-1320 |  |  |  | FV-1321 |  |  |  | FV-1325 |  |  |  | FV-1330 |  |  |  |  | FV-1331 |  |  |  | FV-1340 |  |  |  | FV-1341 |  |  |  | FV-1350 |  |  |  |  | FV-1352 |  |  |  | FV-1355 |  |  |  | FV-1356 |  |  |  | FV-1356-1 |  |  |  |  | FV-1357 |  |  |  | FV-1358 |  |  |  | FV-1359 |  |  |  | FV-1361 |  |  |  |  | FV-1366 |  |  |  | FV-1368 |  |  |  | FV-1804 |  |  |  | FV-1820 |  |  |  |  | FV-1830 |  |  |  | FV-1836 | [6 empty] | LV-1112 |  |  |  |  | LV-1147 |  |  |  | LV-1161 | [6 empty] | LV-1210 |  |  |  |  | LV-1220 |  |  |  | LV-1317 |  |  |  | LV-1320 |  |  |  | LV-1330 |  |  |  |  | LV-1351A |  |  |  | LV-1351B |  |  |  | LV-1360 |  |  |  | LV-1415 |  |  |  |  | LV-1812 |  |  |  | LV-1813 |  |  |  | LV-1815 |  |  |  | LV-1820 |  |  |  |  | LV-1900 | [9 empty] | PV-1119 |  |  |  |  | PV-1214 |  |  |  | PV-1223 |  |  |  | PV-1224 |  |  |  | PV-1317 |  |  |  |  | PV-1324 |  |  |  | PV-1370A |  |  |  | PV-1370B |  |  |  | PV-1400 | [13 empty] | PV-1415 |  |  |  |  | PV-1417 |  |  |  | PV-1420AA |  |  |  | PV-1420AB |  |  |  | PV-1420BA |  |  |  |  | PV-1420BB |  |  |  | PV-1811 |  |  |  | PV-1812 |  |  |  | PV-1814A |  |  |  |  | PV-1814B |  |  |  | PV-1841 |  |  |  | PV-1846 |  |  |  | TV-1154 |  |  |  |  | TV-1165 |  |  |  | TV-1212 |  |  |  | TV-1313 |  |  |  | TV-1345 |  |  |  |  | TV-1348 |  |  |  | TV-1353 |  |  |  | TV-1368 |  |  |  | TV-1383 |  |  |  |  | TV-1384 |  |  |  | TV-1386A |  |  |  | TV-1386B |  |  |  | TV-1389A |  |  |  |  | TV-1389B |  |  |  | TV-1390A |  |  |  | TV-1390B |  |  |  | TV-1395A |  |  |  |  | TV-1397 |  |  |  | TV-1811 |  |  |  | TV-1812 |  |  |  | TV-1813A |  |  |  |  | TV-1813B |  |  |  | TV-1815 | [6 empty] | HV-1118 |  |  |  |  | HV-1119 |  |  |  | HV-1136A |  |  |  | HV-1146 |  |  |  | HV-1166 |  |  |  |  | HV-1228 |  |  |  | HV-1354 |  |  |  | HV-1355 |  |  |  | 108
2 |  | P&ID No. |  |  | D-1-IPA-1001 |  |  |  |  | D-1-IPA-1001 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-2001 |  |  |  |  | D-1-IPA-2001 |  |  |  | D-1-IPA-2001 |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-2002 |  |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3001 |  |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3001 |  |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3002 |  |  |  |  | D-1-IPA-3002 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3004 |  |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3005 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3007 |  |  |  | D-1-IPA-3006 |  |  |  |  | D-1-IPA-3006 |  |  |  | D-1-IPA-3006 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8012 |  |  |  |  | D-1-IPA-8013 |  |  |  | D-1-IPA-8013 | [6 empty] | D-1-IPA-1001 |  |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1003 | [6 empty] | D-1-IPA-2001 |  |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3002 |  |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3006 |  |  |  | D-1-IPA-4001 |  |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8012 |  |  |  |  | D-1-IPA-8024 | [9 empty] | D-1-IPA-1001 |  |  |  |  | D-1-IPA-2001 |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-3001 |  |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3007 |  |  |  | D-1-IPA-3007 |  |  |  | B-1-9112 | [13 empty] | D-1-IPA-4001 |  |  |  |  | D-1-IPA-4001 |  |  |  | D-1-IPA-4002 |  |  |  | D-1-IPA-4002 |  |  |  | D-1-IPA-4002 |  |  |  |  | D-1-IPA-4002 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8014 |  |  |  | D-1-IPA-8014 |  |  |  | D-1-IPA-1002 |  |  |  |  | D-1-IPA-1003 |  |  |  | D-1-IPA-2001 |  |  |  | D-1-IPA-3001 |  |  |  | D-1-IPA-3003 |  |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3006 |  |  |  | D-1-IPA-3003 |  |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3003 |  |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3003 |  |  |  | D-1-IPA-3005 |  |  |  |  | D-1-IPA-3005 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 |  |  |  |  | D-1-IPA-8011 |  |  |  | D-1-IPA-8011 | [6 empty] | D-1-IPA-1001 |  |  |  |  | D-1-IPA-1001 |  |  |  | D-1-IPA-1001 |  |  |  | D-1-IPA-1002 |  |  |  | D-1-IPA-1003 |  |  |  |  | D-1-IPA-2002 |  |  |  | D-1-IPA-3004 |  |  |  | D-1-IPA-3004
3 |  | Service |  |  | FRESH PP TO EA-112 |  |  |  |  | GA-115A/B MIN. FLOW |  |  |  | GAS BLEED TO DA-210 |  |  |  | WASH WATER TO DA-140 |  |  |  | HP STEAM TO EA-211 |  |  |  |  | DA-210 REFLUX |  |  |  | DA-220 FEED INLET |  |  |  | LP STEAM TO EA-221 |  |  |  | DA-220 REFLUX |  |  |  |  | EA-225 VENT GAS |  |  |  | GA-226A/B DISCHARGE |  |  |  | MP STEAM TO EA-311 SHELL SIDE |  |  |  | DA-310 FEED INLET |  |  |  |  | WASH WATER TO DA-310 |  |  |  | DA-310 REFLUX |  |  |  | ETHER TO EA-112 |  |  |  | ETHER TO WWT |  |  |  |  | DA-320 FEED INLET |  |  |  | MP STEAM TO EA-321 |  |  |  | DA-320 REFLUX |  |  |  | DA-330 FEED INLET |  |  |  |  | LP STEAM TO EA-331 |  |  |  | ACETONE TO WWT |  |  |  | DA-320 OVHD TO DA-340 |  |  |  | GA-353A/B DISCHARGE |  |  |  |  | MP STEAM TO EA-352 |  |  |  | WT TO EA-355 OUTLET |  |  |  | DA-360 FEED INLET |  |  |  | GA-356A/B DISCHARGE |  |  |  |  | DA-350 FEED REFLUX |  |  |  | DA-350 FEED INLET |  |  |  | GA-371B DISCHARGE |  |  |  | LP STEAM TO EA-361 |  |  |  |  | GA-365A/B DISCHARGE |  |  |  | DA-360 REFLUX |  |  |  | CL TO CW BASIN |  |  |  | CW BLOW DOWN |  |  |  |  | MP STEAM TO DA-830 |  |  |  | WT TO DA-830 INLET | [6 empty] | HE-1112 OUTLET |  |  |  |  | FC-120 OUTLET |  |  |  | GA-163A/B DISCHARGE | [6 empty] | DA-210 BOTTOMS |  |  |  |  | DA-220 BOTTOMS |  |  |  | PDI TO FC-315 |  |  |  | EA-324 OUTLET |  |  |  | GA-333A/B DISCHARGE |  |  |  |  | EA-351AOUTLET |  |  |  | EA-351BOUTLET |  |  |  | GA-363A/B DISCHARGE |  |  |  | PPR TO FA-415 |  |  |  |  | CL TO FA-815 INLET |  |  |  | CM TO FC-812 INLET |  |  |  | GA-815A/B DISCHARGE. |  |  |  | RAW WATER TO EF-820 |  |  |  |  | PW TO DA-900 INLET | [9 empty] | HP STEAM TO EA-110 |  |  |  |  | EA-217 VAPOR OUTLET |  |  |  | EA-225 WCR |  |  |  | GA-226A/B BYPASS |  |  |  | GA-316A/B MIN. FLOW |  |  |  |  | DA-320 OVHD TO EA-345 |  |  |  | N2 TO FA-373A/B/C |  |  |  | VENT GAS |  |  |  | GA-410A/B MIN. FLOW | [13 empty] | FA-415 VENT TO FLARE |  |  |  |  | GA-415A/B MIN. FLOW |  |  |  | N2 TO FB-420A |  |  |  | FB-420A VENT |  |  |  | N2 TO FB-420B |  |  |  |  | FB-420B VENT |  |  |  | HS TO BG-801 INLET |  |  |  | SM TO BG-802 INLET |  |  |  | SM TO SL-CONSUMERS |  |  |  |  | LP STEAM TO EA-815 |  |  |  | AIR TO FA-841 |  |  |  | N2 TO HEADER |  |  |  | EA-140 WCR |  |  |  |  | EA-165 WCR |  |  |  | EA-215 WCR |  |  |  | EA-316 WCR |  |  |  | EA-345 WCR |  |  |  |  | EA-325 WCR |  |  |  | EA-353A/B WCR |  |  |  | EA-365A/B WCR |  |  |  | EA-327 WCR |  |  |  |  | EA-324 WCR |  |  |  | EA-323A/B WT BYPASS |  |  |  | EA-323A/B OUTLET |  |  |  | PWW TO GA-145A/B |  |  |  |  | PWW TO GA-145A/B |  |  |  | PWW TO DA-310 |  |  |  | PWW TO DA-310 |  |  |  | EA-355 WCR |  |  |  |  | EA-357 WCR |  |  |  | B.F.W TO BG-801 INLET |  |  |  | C.L TO BG-802 INLET |  |  |  | CL EA-812 BYPASS |  |  |  |  | CL EA-812 |  |  |  | EA-815 WCR | [6 empty] | N2 TO DC-110 |  |  |  |  | DC-110 VENT TO FLARE |  |  |  | PPW TO EA-112 |  |  |  | FC-120 VENT TO FLARE |  |  |  | FC-165 VENT TO FLARE |  |  |  |  | FA-223 LIQUID OUTLET |  |  |  | ORGANIC PHASE TO FA-354 |  |  |  | FA-354 OUTLET
4 |  | Line Class |  |  | BB59C1 |  |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BA59C |  |  |  |  | BB57C1 |  |  |  | BB57C1 |  |  |  | BB55C |  |  |  | BB59C1 |  |  |  |  | BB57C1 |  |  |  | BB59C1 |  |  |  | BB57C |  |  |  | BB55C1 |  |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB59C1 |  |  |  | BB55C1 |  |  |  |  | BB55C1 |  |  |  | BB57C |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  |  | BB57C |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C |  |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C |  |  |  | BB55C |  |  |  |  | BB57C |  |  |  | BB55C1 | [6 empty] | FF59C |  |  |  |  | BB59C1 |  |  |  | BB55C1 | [6 empty] | BB57C1 |  |  |  |  | BB57C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB57C1 |  |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  |  | FF55C1 | [9 empty] | BA59C |  |  |  |  | BB57C1 |  |  |  | BB55C |  |  |  | BB57C1 |  |  |  | BB59C1 |  |  |  |  | BB55C1 |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB57C1 | [13 empty] | BB57C1 |  |  |  |  | BB59C1 |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  |  | BB55C |  |  |  | BA59C |  |  |  | BA59C |  |  |  | BB57C |  |  |  |  | BB55C |  |  |  | BB57C |  |  |  | BB59C |  |  |  | BB55C |  |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  | BB55C |  |  |  |  | BB55C |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C |  |  |  |  | BB55C |  |  |  | A1A |  |  |  | BB55C |  |  |  | BB55C |  |  |  |  | BB55C |  |  |  | BB55C | [6 empty] | BB59C |  |  |  |  | BB59C |  |  |  | BB59C1 |  |  |  | BB59C1 |  |  |  | BB55C |  |  |  |  | BB55C1 |  |  |  | BB55C1 |  |  |  | BB55C1
5 |  | Line Size |  | Line Schedule | 2" |  |  |  |  | 3" |  |  |  | 1" |  |  |  | 4" |  |  |  | 1 1/2" |  |  |  |  | 2" |  |  |  | 2" |  |  |  | 4" |  |  |  | 2" |  |  |  |  | 1" |  |  |  | 2" |  |  |  | 6" |  |  |  | 4" |  |  |  |  | 4" |  |  |  | 1" |  |  |  | 1" |  |  |  | 1" |  |  |  |  | 6" |  |  |  | 8" |  |  |  | 3" |  |  |  | 1 1/2" |  |  |  |  | 6" |  |  |  | 1" |  |  |  | 4" |  |  |  | 2" |  |  |  |  | 6" |  |  |  | 1" |  |  |  | 1" |  |  |  | 1" |  |  |  |  | 4" |  |  |  | 2" |  |  |  | 1 1/2" |  |  |  | 4" |  |  |  |  | 1" |  |  |  | 1" |  |  |  | X" |  |  |  | X" |  |  |  |  | 4" |  |  |  | 3" | [6 empty] | 3" |  |  |  |  | 1" |  |  |  | 1 1/2" | [6 empty] | 1 1/2" |  |  |  |  | 1" |  |  |  | 2" |  |  |  | 3" |  |  |  | 1" |  |  |  |  | 3" |  |  |  | 3" |  |  |  | 1" |  |  |  | 2" |  |  |  |  | 4" |  |  |  | 3" |  |  |  | 4" |  |  |  | 6" |  |  |  |  | 1" | [9 empty] | 6" |  |  |  |  | 1" |  |  |  | 4" |  |  |  | 1" |  |  |  | 1" |  |  |  |  | 10" |  |  |  | 2" |  |  |  | 2" |  |  |  | 2" | [13 empty] | 2" |  |  |  |  | 2" |  |  |  | 3" |  |  |  | 4" |  |  |  | 3" |  |  |  |  | 4" |  |  |  | 6" |  |  |  | 6" |  |  |  | 3" |  |  |  |  | 3" |  |  |  | 2" |  |  |  | 2" |  |  |  | 8" |  |  |  |  | 6" |  |  |  | 6" |  |  |  | 6" |  |  |  | 3" |  |  |  |  | 8" |  |  |  | 4" |  |  |  | 6" |  |  |  | 1" |  |  |  |  | 6" |  |  |  | 2" |  |  |  | 3" |  |  |  | 6" |  |  |  |  | 2" |  |  |  | 6" |  |  |  | 2" |  |  |  | 10" |  |  |  |  | 1 1/2" |  |  |  | 1 1/2" |  |  |  | X" |  |  |  | 2" |  |  |  |  | 3" |  |  |  | 6" | [6 empty] | 2" |  |  |  |  | 4" |  |  |  | 3" |  |  |  | 3" |  |  |  | 4" |  |  |  |  | 1" |  |  |  | 1" |  |  |  | 1"
6 |  | Nace Requirement
7 |  | Enclosure Class |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 | [6 empty] | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 | [6 empty] | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 | [9 empty] | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 | [13 empty] | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 | [6 empty] | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56 |  |  |  | Ex d IIB T4, IP56
8
9 | SERVICE CONDITION | Fluid |  |  | PPF |  |  |  |  | PPW |  |  |  | PRG |  |  |  | PWW |  |  |  | SH |  |  |  |  | PPR |  |  |  | PPR |  |  |  | SL |  |  |  | PPR |  |  |  |  | PRG |  |  |  | PPR |  |  |  | SM |  |  |  | PDI |  |  |  |  | PWW |  |  |  | PDI |  |  |  | PE |  |  |  | PE |  |  |  |  | PDI |  |  |  | SM |  |  |  | PDI |  |  |  | PDI |  |  |  |  | SL |  |  |  | PDI |  |  |  | PDI |  |  |  | PIP |  |  |  |  | SM |  |  |  | WT |  |  |  | PDI |  |  |  | PDI |  |  |  |  | PS |  |  |  | PDI |  |  |  | PDI |  |  |  | SL |  |  |  |  | PDI |  |  |  | PDI |  |  |  | CL |  |  |  | WCS |  |  |  |  | SM |  |  |  | WT | [6 empty] | PDI |  |  |  |  | PDI |  |  |  | PDI | [6 empty] | PHE |  |  |  |  | PHE |  |  |  | PDI |  |  |  | WW |  |  |  | PDI |  |  |  |  | PDI |  |  |  | PDI |  |  |  | PPW |  |  |  | PPR |  |  |  |  | CL |  |  |  | CM |  |  |  | CL |  |  |  | WR |  |  |  |  | PW | [9 empty] | SH |  |  |  |  | PRG |  |  |  | WCR |  |  |  | PPR |  |  |  | PE |  |  |  |  | PDI |  |  |  | GFL |  |  |  | GFL |  |  |  | PPR | [13 empty] | VFL |  |  |  |  | PPR |  |  |  | NL |  |  |  | VS |  |  |  | NL |  |  |  |  | VS |  |  |  | HS |  |  |  | HS |  |  |  | SM |  |  |  |  | SL |  |  |  | AI |  |  |  | NH |  |  |  | WCR |  |  |  |  | WCR |  |  |  | WCR |  |  |  | WCR |  |  |  | WCR |  |  |  |  | WCR |  |  |  | WCR |  |  |  | WCR |  |  |  | WCR |  |  |  |  | WCR |  |  |  | WT |  |  |  | WT |  |  |  | PWW |  |  |  |  | PWW |  |  |  | PWW |  |  |  | PWW |  |  |  | WCR |  |  |  |  | WCR |  |  |  | BFW |  |  |  | LC |  |  |  | CL |  |  |  |  | CL |  |  |  | WCR | [6 empty] | NH |  |  |  |  | PRG |  |  |  | PPW |  |  |  | VFL |  |  |  | VFL |  |  |  |  | PHE |  |  |  | PS |  |  |  | PS
10 |  | Flow Rate Unit |  | State | m3/h |  |  |  | L | m3/h |  |  | L | kg/h |  |  | V | m3/h |  |  | L | kg/h |  |  |  | V | m3/h |  |  | L | m3/h |  |  | L | kg/h |  |  | V | m3/h |  |  |  | L | kg/h |  |  | V | m3/h |  |  | L | kg/h |  |  | S | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | kg/h |  |  | S | m3/h |  |  | L | m3/h |  |  |  | L | kg/h |  |  | S | m3/h |  |  | L | kg/h |  |  | V | m3/h |  |  |  | L | kg/h |  |  | S | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | kg/h |  |  |  | S | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | kg/h |  |  | S | m3/h |  |  | L |  |  |  | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L |  |  |  | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | [6 empty] | kg/h |  |  |  | S | kg/h |  |  | V | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | kg/h |  |  | V | kg/h |  |  | V | kg/h |  |  | V | m3/h |  |  |  | L | [9 empty] | kg/h |  |  |  | V | m3/h |  |  | L | kg/h |  |  | V | kg/h |  |  | V | kg/h |  |  |  | V | kg/h |  |  | V | kg/h |  |  | S | kg/h |  |  | S | kg/h |  |  |  | S | kg/h |  |  | S | kg/h |  |  | V | kg/h |  |  | V | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  |  | L | m3/h |  |  | L | m3/h |  |  | L |  |  |  | kg/h |  |  |  | V | kg/h |  |  | V | m3/h |  |  | L | kg/h |  |  | V | kg/h |  |  |  | V | m3/h |  |  | L | m3/h |  |  | L | m3/h |  |  | L
11 |  |  |  |  | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX | NOR | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR | MIN | MAX | NOR | MIN | MAX | NOR | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR |  | MIN
12 |  | Flow Rate |  |  | 10.7041 |  | 8.9201 |  | - | 7.1608 | 5.9673 |  | - | 2000.928 | 1667.44 |  | - | 38.8374 | 32.3645 |  | - | 333.36 |  | 277.8 |  | - | 10.7776 | 8.9813 |  | - | 10.1242 | 8.4368 |  | - | 1094.4 | 912 |  | - | 7.1242 |  | 5.9369 |  | - | 32.4 | 27 |  | - | 10.38 | 8.65 |  | - | 3631.2 | 3026 |  | - | 71.0568 |  | 59.214 |  | - | 57.7902 | 48.1585 |  | - | 1.2614 | 1.0512 |  | - | 1.2177 | 1.0148 |  | - | 0.14308 |  | 0.11923 |  | - | 136.2515 | 113.5429 |  | - | 13024.8 | 10854 |  | - | 32.3153 | 26.9294 |  | - | 7.2907 |  | 6.0756 |  | - | 1806 | 1505 |  | - | 0.020548 | 0.017123 |  | - | 900 | 750 |  | - | 10.5763 |  | 8.8136 |  | - | 4800 | 587 |  | - | HOLD | HOLD |  | - | 1.8659 | 1.5549 |  | - | 1.9 |  | 1.6 |  | - | 51.2804 | 32.872 |  | - | 12.0202 | 10.0168 |  | - | 7.9995 | 6.6662 |  | - | 849.6 |  | 708 |  | - | 0.84858 | 0.70715 |  | - | 1.1899 | 0.99156 |  | - | HOLD | HOLD |  | - | HOLD |  | HOLD |  | - | 1154.4 | 962 |  | - | 19.7112 | 16.426 |  | - |  |  |  | 20.52 |  | 17.1 |  | - | 2 | 1.6667 |  | - | 1.7532 | 1.461 |  | - |  |  |  | 1.476 |  | 1.23 |  | - | 0.076525 | 0.063771 |  | - | 2.4027 | 2.0022 |  | - | 16.755 | 13.9625 |  | - | 1.4231 |  | 1.1859 |  | - | 17.1654 | 14.3045 |  | - | 17.1661 | 14.3051 |  | - | 1.0946 | 0.91215 |  | - | 12.109 |  | 9.1302 |  | - | 21850.8 | 18209 |  | - | 6591.444 | 5571.34 |  | - | HOLD | HOLD |  | - | 41.8169 |  | 30.7602 |  | - | HOLD | HOLD |  | - | [6 empty] | 7011.6 |  | 5843 |  | - | 55 | - |  | - | 54.2496 | 45.208 |  | - | 3.114 | 2.595 |  | - | 0.40823 |  | 0.34019 |  | - | 6284.4 | 5237 |  | - | 75 | 62.5 |  | - | 75 | 62.5 |  | - | [14 empty] | 18.48 |  | 15.4 |  | - | 5.22 | 4.35 |  | - | 125.85 | 104.875 |  | - | 935.4 | 779.5 |  | - | 125.85 |  | 104.875 |  | - | 935.4 | 779.5 |  | - | 6770 | 5722 |  | - | 20195 | 14088 |  | - | 1379.419 |  | 1190 |  | - | 1379.419 | 1190 |  | - | HOLD | HOLD |  | - | 714 | 714 |  | - | 314.6379 |  | 262.1982 |  | - | 62.3006 | 51.9171 |  | - | 175.9143 | 146.5952 |  | - | 99.611 | 83.0092 |  | - | 29.3029 |  | 24.419 |  | - | 281.9256 | 234.938 |  | - | 36.994 | 30.8283 |  | - | 34.871 | 29.0592 |  | - | 1.2096 |  | 1.008 |  | - | 159.8851 | 133.2376 |  | - | 18.9236 | 15.7697 |  | - | 19.3876 | 16.1564 |  | - | 37.5968 |  | 31.3307 |  | - | 1.9434 | 1.6195 |  | - | 55.01 | 45.8417 |  | - | 2.8434 | 2.3695 |  | - | 614.5623 |  | 512.1352 |  | - | 6.0502 | 5.0418 |  | - | 589.2 | 491 |  | - | HOLD | HOLD |  | - | 21850.8 |  | 18209 |  | - | 21850.8 | 18209 |  | - | 81541.2 | 67951 |  | - |  |  |  | 714 |  | 714 |  | - | 13200 | - |  | - | 23.8692 | 19.891 |  | - | 7700 | - |  | - | 1000 |  | - |  | - | 1.086 | - |  | - | 51.3 | 32.9 |  | - | 1.2468 | - |  | -
13 |  | Inlet Pressure |  | (kg/cm2g) | - |  | 49.15 |  | - | - | 49.8 |  | - | - | 44.8 |  | - | - | 39.05 |  | - | - |  | 31 |  | - | - | 22.9 |  | - | - | 22.9 |  | - | - | 3.5 |  | - | - |  | 22.15 |  | - | - | 19 |  | - | - | 50.92 |  | - | - | 9.8 |  | - | - |  | 4.98 |  | - | - | 4 |  | - | - | 5.2 |  | - | - | 50.8 |  | - | - |  | 3.6 |  | - | - | 5.7 |  | - | - | 9.8 |  | - | - | 7.97 |  | - | - |  | 6.37 |  | - | - | 3.5 |  | - | - | 0.5 |  | - | - | 1.6 |  | - | - |  | 4.37 |  | - | - | 9.8 |  | - | - | 5 |  | - | - | 3.44 |  | - | - |  | 3.44 |  | - | - | 4.7 |  | - | - | 1.67 |  | - | - | 5.19 |  | - | - |  | 3.5 |  | - | - | 4.14 |  | - | - | 4.14 |  | - | - | - |  | - | - |  | 5 |  | - | - | 9.8 |  | - | - | 5.35 |  | - |  |  |  | - |  | 32.5 |  | - | - | 31 |  | - | - | 5.5 |  | - |  |  |  | - |  | 16.53 |  | - | - | 19.59 |  | - | - | 0.05 |  | - | - | 4.19 |  | - | - |  | 6.8 |  | - | - | 1.6 |  | - | - | 1.6 |  | - | - | 6.4 |  | - | - |  | 17 |  | - | - | 2 |  | - | - | 9.8 |  | - | - | - |  | - | - |  | 4 |  | - | - | - |  | - | [6 empty] | - |  | 31 |  | - | - | 16.4 |  | - | - | 4.3 |  | - | - | 50.92 |  | - | - |  | 50.8 |  | - | - | 1.6 |  | - | - | 2 |  | - | - | 0.03 |  | - | [14 empty] | - |  | 15.2 |  | - | - | 49.65 |  | - | - | 2 |  | - | - | ATM |  | - | - |  | 2 |  | - | - | ATM |  | - | - | 40 |  | - | - | 40 |  | - | - |  | 9.8 |  | - | - | 3.5 |  | - | - | 30 |  | - | - | 70 |  | - | - |  | 4.3 |  | - | - | 4.3 |  | - | - | 4.3 |  | - | - | 4.3 |  | - | - |  | 4.3 |  | - | - | 4.3 |  | - | - | 4.3 |  | - | - | 4.3 |  | - | - |  | 4.3 |  | - | - | 4.3 |  | - | - | 6.11 |  | - | - | 5.73 |  | - | - |  | 5.67 |  | - | - | 4.98 |  | - | - | 5.67 |  | - | - | 4.98 |  | - | - |  | 4.3 |  | - | - | 4.3 |  | - | - | 60 |  | - | - | - |  | - | - |  | 3.5 |  | - | - | 3.5 |  | - | - | 4.3 |  | - |  |  |  | - |  | 40 |  | - | - | 39.8 |  | - | - | 49.35 |  | - | - | 31 |  | - | - |  | 0.1 |  | - | - | 5.5 |  | - | - | 3.7 |  | - | - | 0.5 |  | -
14 |  | Pressure Drop |  | (kg/cm2) |  |  | 0.7 |  |  |  | 44.8 |  |  |  | 28 |  |  |  | 4.8 |  |  |  |  | 3 |  |  |  | 4.3 |  |  |  | 0.9 |  |  |  | 1 |  |  |  |  | 0.7 |  |  |  | 13.5 |  |  |  | 2.5 |  |  |  | 1.8 |  |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  |  | 49.7 |  |  |  | 0.8 |  |  |  | 1.6 |  |  |  | 0.7 |  |  |  |  | 0.7 |  |  |  | 1 |  |  |  | 0.2 |  |  |  | 1.2 |  |  |  |  | 0.7 |  |  |  | 1.8 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 1.5 |  |  |  | 0.7 |  |  |  |  | 1 |  |  |  | 0.7 |  |  |  | 0.93 |  |  |  | - |  |  |  |  | - |  |  |  | 1.8 |  |  |  | 4 | [7 empty] | 0.7 |  |  |  | 30 |  |  |  | 0.8 | [7 empty] | 11.28 |  |  |  | 14 |  |  |  | 0.8 |  |  |  | 3 |  |  |  |  | 0.8 |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.7 |  |  |  |  | 0.7 |  |  |  | 0.9 |  |  |  | 1.8 |  |  |  | - |  |  |  |  | - |  |  |  | - | [10 empty] | 3 |  |  |  | 15.6 |  |  |  | 0.7 |  |  |  | 30.8 |  |  |  |  | 49.8 |  |  |  | 0.6 |  |  |  | 1.95 |  |  |  | 0.03 | [18 empty] | 14.9 |  |  |  | 33.5 |  |  |  | 1.95 |  |  |  | - |  |  |  |  | 1.95 |  |  |  | - |  |  |  | 9 |  |  |  | 30.2 |  |  |  |  | 6.3 |  |  |  | 1 |  |  |  | 22.5 |  |  |  | 25 |  |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  |  | 0.7 |  |  |  | 0.7 |  |  |  | 29 |  |  |  | - |  |  |  |  | 1.5 |  |  |  | 1.5 |  |  |  | 0.7 | [7 empty] | 0.2 |  |  |  | 39.5 |  |  |  | 0.9 |  |  |  | 30.7 |  |  |  |  | 0.1 |  |  |  | 0.7 |  |  |  | 3.7 |  |  |  | 0.2
15 |  | Temperature |  | (deg C) | - |  | 25 |  | - | - | 103 |  | - | - | 125 |  | - | - | 95 |  | - | - |  | 255 |  | - | - | 40 |  | - | - | 40 |  | - | - | 147 |  | - | - |  | 48.3 |  | - | - | 47.2 |  | - | - | 47.2 |  | - | - | 198 |  | - | - |  | 82.39 |  | - | - | 95 |  | - | - | 45 |  | - | - | 45 |  | - | - |  | 53.1 |  | - | - | 122 |  | - | - | 198 |  | - | - | 50.19 |  | - | - |  | 111.3 |  | - | - | 147 |  | - | - | 56 |  | - | - | 105.62 |  | - | - |  | 89.94 |  | - | - | 198 |  | - | - | AMB |  | - | - | 40.3 |  | - | - |  | 40.3 |  | - | - | 40 |  | - | - | 106.38 |  | - | - | 40 |  | - | - |  | 147 |  | - | - | 74.07 |  | - | - | 74.07 |  | - | - | 100 |  | - | - |  | 32 |  | - | - | 198 |  | - | - | 100 |  | - |  |  |  | - |  | 122 |  | - | - | 93.9 |  | - | - | 78 |  | - |  |  |  | - |  | 173 |  | - | - | 54.1 |  | - | - | 45 |  | - | - | 40 |  | - | - |  | 117.31 |  | - | - | 105.62 |  | - | - | 106 |  | - | - | 108.2 |  | - | - |  | 31 |  | - | - | 126.5 |  | - | - | 182 |  | - | - | 100 |  | - | - |  | AMB |  | - | - | 150 |  | - | [6 empty] | - |  | 255 |  | - | - | 39 |  | - | - | 42 |  | - | - | 47.2 |  | - | - |  | 45 |  | - | - | 105.6 |  | - | - | AMB |  | - | - | 40 |  | - | [14 empty] | - |  | AMB |  | - | - | 25 |  | - | - | AMB |  | - | - | AMB |  | - | - |  | AMB |  | - | - | AMB |  | - | - | 340 |  | - | - | 340 |  | - | - |  | 197 |  | - | - | 165 |  | - | - | AMB |  | - | - | AMB |  | - | - |  | 42 |  | - | - | 38 |  | - | - | 36 |  | - | - | 42 |  | - | - |  | 38 |  | - | - | 42 |  | - | - | 40 |  | - | - | 42 |  | - | - |  | 42 |  | - | - | 39.8 |  | - | - | 20 |  | - | - | 75.9 |  | - | - |  | 97.89 |  | - | - | 40 |  | - | - | 97.89 |  | - | - | 40 |  | - | - |  | 40 |  | - | - | 42 |  | - | - | 120 |  | - | - | 100 |  | - | - |  | 147 |  | - | - | 126.5 |  | - | - | 42 |  | - |  |  |  | - |  | AMB |  | - | - | 192 |  | - | - | 103 |  | - | - | 93.9 |  | - | - |  | 38 |  | - | - | 20 |  | - | - | 40 |  | - | - | 30 |  | -
16 |  | Travel |  | (%)
17 |  | Max. Allowable Sound Level |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA | [6 empty] | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA | [6 empty] | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA | [9 empty] | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA | [13 empty] | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA | [6 empty] | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  |  | 85 dBA |  |  |  | 85 dBA |  |  |  | 85 dBA
18 |  | Calculated Cv |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * | [6 empty] | * |  |  |  |  | * |  |  |  | * | [6 empty] | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * | [9 empty] | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * | [13 empty] | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * | [6 empty] | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | *
19 |  | Selected Valve Cv |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * | [6 empty] | * |  |  |  |  | * |  |  |  | * | [6 empty] | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * | [9 empty] | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * | [13 empty] | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * | [6 empty] | * |  |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  | * |  |  |  |  | * |  |  |  | * |  |  |  | *
20 |  | Shut-Off ΔP |  | (kg/cm2) | 55 |  |  |  |  | 61.1 |  |  |  | 55 |  |  |  | 48.1 |  |  |  | 46 |  |  |  |  | 31.7 |  |  |  | 31.7 |  |  |  | 6 |  |  |  | 28.3 |  |  |  |  | 25 |  |  |  | 55 |  |  |  | 12 |  |  |  | 7.9 |  |  |  |  | 8 |  |  |  | 7.4 |  |  |  | 63.5 |  |  |  | 5.7 |  |  |  |  | 7.8 |  |  |  | 12 |  |  |  | 10.2 |  |  |  | 8.5 |  |  |  |  | 6 |  |  |  | 2 |  |  |  | 4 |  |  |  | 6.2 |  |  |  |  | 12 |  |  |  | 7 |  |  |  | 5.7 |  |  |  | 5.7 |  |  |  |  | 7.1 |  |  |  | 4 |  |  |  | 6.7 |  |  |  | 6 |  |  |  |  | 6.9 |  |  |  | 6.9 |  |  |  | - |  |  |  | 7 |  |  |  |  | 12 |  |  |  | 10 | [6 empty] | 36 |  |  |  |  | 55 |  |  |  | 7.6 | [6 empty] | 25 |  |  |  |  | 25 |  |  |  | 6 |  |  |  | 10.6 |  |  |  | 8.9 |  |  |  |  | 4 |  |  |  | 4 |  |  |  | 10 |  |  |  | 25 |  |  |  |  | 6 |  |  |  | 12 |  |  |  | - |  |  |  | 7 |  |  |  |  | - | [9 empty] | 46 |  |  |  |  | 25 |  |  |  | 7 |  |  |  | 55 |  |  |  | 63.5 |  |  |  |  | 4 |  |  |  | 10 |  |  |  | 0.5 | [17 empty] | 18.5 |  |  |  |  | 58.6 |  |  |  | 10 |  |  |  | 0.12 |  |  |  | 10 |  |  |  |  | 0.12 |  |  |  | 45 |  |  |  | 45 |  |  |  | 12 |  |  |  |  | 6 |  |  |  | 77 |  |  |  | 77 |  |  |  | 7 |  |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  |  | 7 |  |  |  | 10 |  |  |  | 10 |  |  |  | 8 |  |  |  |  | 8 |  |  |  | 8 |  |  |  | 8 |  |  |  | 7 |  |  |  |  | 7 |  |  |  | - |  |  |  | - |  |  |  | 6 |  |  |  |  | 6 |  |  |  | 7 | [6 empty] | 77 |  |  |  |  | 77 |  |  |  | 61.1 |  |  |  | 55 |  |  |  | 2 |  |  |  |  | 20 |  |  |  | 7.1 |  |  |  | 2
21 |  | Design Press. |  | (kg/cm2g) | 55 |  |  |  |  | 61.1 |  |  |  | 55 |  |  |  | 48.1 |  |  |  | 46 |  |  |  |  | 31.7 |  |  |  | 31.7 |  |  |  | 6 |  |  |  | 28.3 |  |  |  |  | 25 |  |  |  | 55 |  |  |  | 12 |  |  |  | 7.9 |  |  |  |  | 8 |  |  |  | 7.4 |  |  |  | 63.5 |  |  |  | 5.7 |  |  |  |  | 7.8 |  |  |  | 12 |  |  |  | 10.2 |  |  |  | 8.5 |  |  |  |  | 6 |  |  |  | 2 |  |  |  | 4 |  |  |  | 6.2 |  |  |  |  | 12 |  |  |  | 7 |  |  |  | 5.7 |  |  |  | 5.7 |  |  |  |  | 7.1 |  |  |  | 4 |  |  |  | 6.7 |  |  |  | 6 |  |  |  |  | 6.9 |  |  |  | 6.9 |  |  |  | - |  |  |  | 7 |  |  |  |  | 12 |  |  |  | 10 | [6 empty] | 36 |  |  |  |  | 55 |  |  |  | 7.6 | [6 empty] | 25 |  |  |  |  | 25 |  |  |  | 6 |  |  |  | 10.6 |  |  |  | 8.9 |  |  |  |  | 4 |  |  |  | 4 |  |  |  | 10 |  |  |  | 25 |  |  |  |  | 6 |  |  |  | 12 |  |  |  | - |  |  |  | 7 |  |  |  |  | - | [9 empty] | 46 |  |  |  |  | 25 |  |  |  | 7 |  |  |  | 55 |  |  |  | 63.5 |  |  |  |  | 4 |  |  |  | 10 |  |  |  | 0.5 | [17 empty] | 18.5 |  |  |  |  | 58.6 |  |  |  | 10 |  |  |  | 0.12 |  |  |  | 10 |  |  |  |  | 0.12 |  |  |  | 45 |  |  |  | 45 |  |  |  | 12 |  |  |  |  | 6 |  |  |  | 77 |  |  |  | 77 |  |  |  | 7 |  |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  |  | 7 |  |  |  | 10 |  |  |  | 10 |  |  |  | 8 |  |  |  |  | 8 |  |  |  | 8 |  |  |  | 8 |  |  |  | 7 |  |  |  |  | 7 |  |  |  | - |  |  |  | - |  |  |  | 6 |  |  |  |  | 6 |  |  |  | 7 | [6 empty] | 77 |  |  |  |  | 77 |  |  |  | 61.1 |  |  |  | 55 |  |  |  | 2 |  |  |  |  | 20 |  |  |  | 7.1 |  |  |  | 2
22 |  | Design Temp. |  | (deg C) | 65 |  |  |  |  | 180 |  |  |  | 180 |  |  |  | 150 |  |  |  | 400 |  |  |  |  | 120 |  |  |  | 120 |  |  |  | 200 |  |  |  | 120 |  |  |  |  | 120 |  |  |  | 120 |  |  |  | 250 |  |  |  | 120 |  |  |  |  | 150 |  |  |  | 120 |  |  |  | 120 |  |  |  | 120 |  |  |  |  | 150 |  |  |  | 250 |  |  |  | 140 |  |  |  | 180 |  |  |  |  | 200 |  |  |  | 82 |  |  |  | 180 |  |  |  | 120 |  |  |  |  | 250 |  |  |  | AMB |  |  |  | 120 |  |  |  | 120 |  |  |  |  | 120 |  |  |  | 180 |  |  |  | 120 |  |  |  | 200 |  |  |  |  | 120 |  |  |  | 120 |  |  |  | HOLD |  |  |  | 60 |  |  |  |  | 250 |  |  |  | 160 | [6 empty] | 250 |  |  |  |  | 120 |  |  |  | 120 | [6 empty] | 200 |  |  |  |  | 120 |  |  |  | 150 |  |  |  | 150 |  |  |  | 160 |  |  |  |  | 120 |  |  |  | 120 |  |  |  | 140 |  |  |  | 48 |  |  |  |  | 180 |  |  |  | 250 |  |  |  | HOLD |  |  |  | 60 |  |  |  |  | HOLD | [9 empty] | 400 |  |  |  |  | 120 |  |  |  | 50 |  |  |  | 120 |  |  |  | 120 |  |  |  |  | 180 |  |  |  | 60 |  |  |  | 60 | [17 empty] | 65 |  |  |  |  | 65 |  |  |  | 60 |  |  |  | 120 |  |  |  | 60 |  |  |  |  | 120 |  |  |  | 425 |  |  |  | 425 |  |  |  | 250 |  |  |  |  | 200 |  |  |  | 65 |  |  |  | 65 |  |  |  | 50 |  |  |  |  | 50 |  |  |  | 50 |  |  |  | 50 |  |  |  | 50 |  |  |  |  | 50 |  |  |  | 50 |  |  |  | 50 |  |  |  | 50 |  |  |  |  | 50 |  |  |  | 150 |  |  |  | 150 |  |  |  | 150 |  |  |  |  | 150 |  |  |  | 150 |  |  |  | 150 |  |  |  | 50 |  |  |  |  | 50 |  |  |  | HOLD |  |  |  | HOLD |  |  |  | 180 |  |  |  |  | 180 |  |  |  | 60 | [6 empty] | 65 |  |  |  |  | 280 |  |  |  | 180 |  |  |  | 120 |  |  |  | 120 |  |  |  |  | 120 |  |  |  | 120 |  |  |  | 120
23 |  | Vapor Press. |  | (kg/cm2) | 11.95 |  |  |  |  | 1.27 |  |  |  | - |  |  |  | 0.89 |  |  |  | - |  |  |  |  | 17.23 |  |  |  | 17.81 |  |  |  | - |  |  |  | 20.51 |  |  |  |  | - |  |  |  | 23.15 |  |  |  | - |  |  |  | 1.24 |  |  |  |  | 1.31 |  |  |  | 0.57 |  |  |  | 0.78 |  |  |  | 0.78 |  |  |  |  | 2.92 |  |  |  | - |  |  |  | 0.27 |  |  |  | 2.97 |  |  |  |  | - |  |  |  | 0.34 |  |  |  | - |  |  |  | 1.4 |  |  |  |  | - |  |  |  | 0.0321 |  |  |  | 0.41 |  |  |  | 0.41 |  |  |  |  | 0.53 |  |  |  | 2.7 |  |  |  | 0.14 |  |  |  | - |  |  |  |  | 1.05 |  |  |  | 1.05 |  |  |  | - |  |  |  | 0.0485 |  |  |  |  | - |  |  |  | - | [6 empty] | 33.53 |  |  |  |  | 32.03 |  |  |  | 1.23 | [6 empty] | 17.56 |  |  |  |  | 20.62 |  |  |  | 0.57 |  |  |  | 0.06 |  |  |  | 3.12 |  |  |  |  | 2.53 |  |  |  | 2.53 |  |  |  | 1.38 |  |  |  | 12.5956 |  |  |  |  | 2.479 |  |  |  | 10.8332 |  |  |  | - |  |  |  | 0.0239 |  |  |  |  | - | [9 empty] | - |  |  |  |  | - |  |  |  | 0.0835 |  |  |  | 23.15 |  |  |  | 0.78 |  |  |  |  | - |  |  |  | - |  |  |  | - | [17 empty] | - |  |  |  |  | 11.95 |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | 14.997 |  |  |  |  | 6.5059 |  |  |  | - |  |  |  | - |  |  |  | 0.0835 |  |  |  |  | 0.0674 |  |  |  | 0.06044 |  |  |  | 0.0835 |  |  |  | 0.0835 |  |  |  |  | 0.0835 |  |  |  | 0.075092 |  |  |  | 0.0835 |  |  |  | 0.0835 |  |  |  |  | 0.075092 |  |  |  | 0.02 |  |  |  | 0.4096 |  |  |  | 0.96 |  |  |  |  | 0.06 |  |  |  | 0.96 |  |  |  | 0.06 |  |  |  | 0.075092 |  |  |  |  | 0.0835 |  |  |  | 2.0258 |  |  |  | - |  |  |  | 4.5332 |  |  |  |  | 2.479 |  |  |  | 0.08 | [6 empty] | - |  |  |  |  | - |  |  |  | 1.27 |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | 0.53 |  |  |  | 0.53
24 |  | Critical Press. |  | (kg/cm2) | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - | [9 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - | [17 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | -
25 |  | S.G. @ Op |  | Density @ Op |  |  |  | 507.17 |  |  |  | 883.3 |  |  |  | 90.02 |  |  |  | 963 |  |  |  |  | 14.24 |  |  |  | 454.4 |  |  |  | 454.4 |  |  |  | 1.87 |  |  |  |  | 465.7 |  |  |  | 43.43 |  |  |  | 436.8 |  |  |  | 5.0955 |  |  |  |  | 880.7 |  |  |  | 962.1 |  |  |  | 969.38 |  |  |  | 681.94 |  |  |  |  | 681.94 |  |  |  | 875.94 |  |  |  | 5.0955 |  |  |  | 787.17 |  |  |  |  | 738.89 |  |  |  | 1.87 |  |  |  | 795.41 |  |  |  | 3.98 |  |  |  |  | 711.52 |  |  |  | 5.0955 |  |  |  | 997.4 |  |  |  | 906.48 |  |  |  |  | 906.48 |  |  |  | 802.1 |  |  |  | 712.8 |  |  |  | 774.8 |  |  |  |  | 2.34 |  |  |  | 764.45 |  |  |  | 764.45 |  |  |  | HOLD |  |  |  |  | 995.255 |  |  |  | 5.0955 |  |  |  | 958.6 | [7 empty] | 839.2 |  |  |  | 855.6 |  |  |  | 739.12 | [7 empty] | 545.28 |  |  |  | 442.21 |  |  |  | 895 |  |  |  | 992.5 |  |  |  |  | 797.2 |  |  |  | 715.23 |  |  |  | 715.2 |  |  |  | 952.58 |  |  |  |  | 495.5 |  |  |  | 937.835 |  |  |  | 4.584 |  |  |  | HOLD |  |  |  |  | 998.39 |  |  |  | HOLD | [10 empty] | 14.2 |  |  |  | 3.99 |  |  |  | 991.7 |  |  |  | 436.8 |  |  |  |  | 681.94 |  |  |  | 3.98 |  |  |  | 8.78 |  |  |  | 8.78 | [18 empty] | 2.26 |  |  |  | 486 |  |  |  | 8.78 |  |  |  | 1.43 |  |  |  |  | 8.78 |  |  |  | 1.43 |  |  |  | 15.48 |  |  |  | 15.48 |  |  |  |  | 5.217 |  |  |  | 2.274 |  |  |  | 83.065 |  |  |  | 79.81 |  |  |  |  | 991.7 |  |  |  | 993.2 |  |  |  | 993.9 |  |  |  | 991.7 |  |  |  |  | 993.2 |  |  |  | 992.1 |  |  |  | 992.4 |  |  |  | 991.7 |  |  |  |  | 992.1 |  |  |  | 992.4 |  |  |  | 998.5 |  |  |  | 974.6 |  |  |  |  | 960.1 |  |  |  | 979.4 |  |  |  | 960.1 |  |  |  | 979.4 |  |  |  |  | 992.4 |  |  |  | 991.7 |  |  |  | 945.98 |  |  |  | HOLD |  |  |  |  | 919.37 |  |  |  | 937.9 |  |  |  | 992 | [7 empty] | 43.9 |  |  |  | 46.49 |  |  |  | 883.3 |  |  |  | 66.39 |  |  |  |  | 1.95 |  |  |  | 552.5 |  |  |  | 802.08 |  |  |  | 802.08
26 |  | Viscosity @ Op. |  | Molcular Mass | 0.0803 |  |  | - |  | 0.272 |  | - |  | 0.0143 |  | 43.87 |  | 0.296 |  | - |  | 0.017 |  |  | 18 |  | 0.065 |  | - |  | 0.065 |  | - |  | 0.014 |  | 18 |  | 0.076 |  |  | - |  | 0.0105 |  | 41.89 |  | 0.056 |  | - |  | 0.016 |  | 18 |  | 0.318 |  |  | - |  | 0.288 |  | - |  | 0.611 |  | - |  | 0.2396 |  | - |  | 0.2396 |  |  | - |  | 0.225 |  | - |  | 0.016 |  | 18 |  | 0.8481 |  | - |  | 0.266 |  |  | - |  | 0.014 |  | 18 |  | 0.727 |  | - |  | 0.011 |  | 46.92 |  | 0.416 |  |  | - |  | 0.016 |  | 18 |  | 0.89 |  | - |  | 0.7083 |  | - |  | 0.7083 |  |  | - |  | 0.727 |  | - |  | 0.2885 |  | - |  | 1.34 |  | - |  | 0.014 |  |  | 18 |  | 0.456 |  | - |  | 0.456 |  | - |  | HOLD |  | - |  | 0.765 |  |  | - |  | 0.016 |  | 18 |  | 0.282 |  | - |  |  |  |  | 0.2187 |  |  | - |  | 0.0111 |  | - |  | 0.3806 |  | - |  |  |  |  | 0.125 |  |  | - |  | 0.0725 |  | - |  | 0.611 |  | - |  | 0.653 |  | - |  | 0.2457 |  |  | - |  | 0.2977 |  | - |  | 0.298 |  | - |  | 0.2593 |  | - |  | 0.074 |  |  | - |  | 0.219 |  | - |  | 0.02 |  | - |  | HOLD |  | - |  | 1.001 |  |  | - |  | HOLD |  | - | [7 empty] | 0.019 |  |  | 18 |  | 0.007 |  | 41.96 |  | 0.629 |  | - |  | 0.056 |  | - |  | 0.2396 |  |  | - |  | 0.011 |  | 46.92 |  | 0.0178 |  | 28 |  | 0.0178 |  | 28 | [15 empty] | 0.009 |  |  | 42.08 |  | 0.0803 |  | - |  | 0.0178 |  | 28 |  | 0.0152 |  | 34.96 |  | 0.0178 |  |  | 28 |  | 0.0152 |  | 34.96 |  | 0.019 |  | 18 |  | 0.02 |  | 18 |  | 0.015 |  |  | 18 |  | 0.01463 |  | 18 |  | 0.02 |  | 28.95 |  | 0.019 |  | 28 |  | 0.63 |  |  | - |  | 0.678 |  | - |  | 0.705 |  | - |  | 0.629 |  | - |  | 0.678 |  |  | - |  | 0.629 |  | - |  | 0.653 |  | - |  | 0.629 |  | - |  | 0.629 |  |  | - |  | 0.653 |  | - |  | 1.001 |  | - |  | 0.374 |  | - |  | 0.2861 |  |  | - |  | 0.6711 |  | - |  | 0.2861 |  | - |  | 0.6711 |  | - |  | 0.653 |  |  | - |  | 0.629 |  | - |  | 0.2335 |  | - |  | HOLD |  | - |  | 0.18585 |  |  | - |  | 0.219 |  | - |  | 0.641 |  | - |  |  |  |  | 0.019 |  |  | 28 |  | 0.0145 |  | 37.11 |  | 0.272 |  | - |  | 0.0127 |  | 43.87 |  | 0.0088 |  |  | 44.71 |  | 0.119 |  | - |  | 0.7273 |  | - |  | 0.7273 |  | -
27 |  | Cp/Cv |  | Comp. Factor | - |  |  | - |  | - |  | - |  | 1.65 |  | - |  | - |  | - |  | 1.1496 |  |  | - |  | - |  | - |  | - |  | - |  | 1.34 |  | - |  | - |  |  | - |  | 1.46 |  | - |  | - |  | - |  | 1.357 |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | 1.357 |  | - |  | - |  | - |  | - |  |  | - |  | 1.34 |  | - |  | - |  | - |  | 1.12 |  | - |  | - |  |  | - |  | 1.357 |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 1.34 |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | 1.357 |  | - |  | - |  | - |  |  |  |  | - |  |  | - |  | - |  | - |  | - |  | - |  |  |  |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - | [7 empty] | 1.1496 |  |  | - |  | 1.21 |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | 1.12 |  | - |  | 1.411 |  | - |  | 1.411 |  | - | [15 empty] | 1.16 |  |  | - |  | - |  | - |  | 1.411 |  | - |  | 1.2448 |  | - |  | 1.411 |  |  | - |  | 1.2448 |  | - |  | 1.41 |  | - |  | 1.41 |  | - |  | 1.396 |  |  | - |  | 1.359 |  | - |  | 1.5112 |  | - |  | 1.5035 |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  |  |  |  | 1.4553 |  |  | - |  | 1.32 |  | - |  | - |  | - |  | 1.57 |  | - |  | 1.14 |  |  | - |  | - |  | - |  | - |  | - |  | - |  | -
28 | BODY & TRIM | Type of Body |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE | [6 empty] | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE | [6 empty] | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE | [9 empty] | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE | [13 empty] | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE | [6 empty] | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  |  | GLOBE |  |  |  | GLOBE |  |  |  | GLOBE
29 |  | Body Size |  | Port Size | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  |  |  |  | * |  |  | * |  | * |  | * |  | * |  | * |  |  |  |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * | [7 empty] | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * | [10 empty] | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  |  |  |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  | * |  |  | * |  | * |  | * |  | * |  | * |  | * |  | *
30 |  | Connection Rating (ANSI) |  |  | 600# RF |  |  |  |  | 600# RF |  |  |  | 600# RF |  |  |  | 600# RF |  |  |  | 600# RF |  |  |  |  | 300# RF |  |  |  | 300# RF |  |  |  | 150# RF |  |  |  | 600# RF |  |  |  |  | 300# RF |  |  |  | 600# RF |  |  |  | 300# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 600# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 300# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 300# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 300# RF |  |  |  | 150# RF | [6 empty] | 600# RF |  |  |  |  | 600# RF |  |  |  | 150# RF | [6 empty] | 300# RF |  |  |  |  | 300# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 300# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF | [9 empty] | 600# RF |  |  |  |  | 300# RF |  |  |  | 150# RF |  |  |  | 300# RF |  |  |  | 600# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF | [13 empty] | 300# RF |  |  |  |  | 600# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 600# RF |  |  |  | 600# RF |  |  |  | 300# RF |  |  |  |  | 150# RF |  |  |  | 300# RF |  |  |  | 600# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 600# RF |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF | [6 empty] | 600# RF |  |  |  |  | 600# RF |  |  |  | 600# RF |  |  |  | 600# RF |  |  |  | 150# RF |  |  |  |  | 150# RF |  |  |  | 150# RF |  |  |  | 150# RF
31 |  | Flange Face Finish |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH | [6 empty] | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH | [6 empty] | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH | [9 empty] | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH | [13 empty] | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH | [6 empty] | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH |  |  |  | 125 ~ 250 AARH
32 |  |  |  | Body | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB | [6 empty] | A351 CF3M |  |  |  |  | A216 WCB |  |  |  | A216 WCB | [6 empty] | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A351 CF3M | [9 empty] | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB | [13 empty] | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB | [6 empty] | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  |  | A216 WCB |  |  |  | A216 WCB |  |  |  | A216 WCB
33 |  |  |  | Plug / Ball / Disk | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST | [6 empty] | 316LSS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST | [6 empty] | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316LSS+ST | [9 empty] | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST | [13 empty] | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST | [6 empty] | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST
34 |  | Material |  | Seat | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST | [6 empty] | 316LSS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST | [6 empty] | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316LSS+ST | [9 empty] | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST | [13 empty] | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST | [6 empty] | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  |  | 316SS+ST |  |  |  | 316SS+ST |  |  |  | 316SS+ST
35 |  |  |  | Stem | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316LSS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316LSS | [9 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS | [13 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS
36 |  |  |  | Guide / Cage | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316LSS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316LSS | [9 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS | [13 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS
37 |  |  |  | Packing | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | GRAPHITE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | GRAPHITE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | GRAPHITE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | GRAPHITE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | GRAPHITE |  |  |  | PTFE | [6 empty] | PTFE |  |  |  |  | PTFE |  |  |  | PTFE | [6 empty] | GRAPHITE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | GRAPHITE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | GRAPHITE | [9 empty] | GRAPHITE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE | [13 empty] | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | GRAPHITE |  |  |  | GRAPHITE |  |  |  | GRAPHITE |  |  |  |  | GRAPHITE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE | [6 empty] | PTFE |  |  |  |  | GRAPHITE |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE |  |  |  |  | PTFE |  |  |  | PTFE |  |  |  | PTFE
38 |  | Type of Bonnet |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | EXTENDED |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | EXTENDED |  |  |  | STANDARD |  |  |  | EXTENDED |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | EXTENDED |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | EXTENDED |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | EXTENDED |  |  |  | STANDARD | [6 empty] | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD | [6 empty] | EXTENDED |  |  |  |  | EXTENDED |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | EXTENDED |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD | [9 empty] | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD | [13 empty] | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD | [6 empty] | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  |  | STANDARD |  |  |  | STANDARD |  |  |  | STANDARD
39 |  | Characteristic |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% | [6 empty] | LINEAR |  |  |  |  | LINEAR |  |  |  | LINEAR | [6 empty] | LINEAR |  |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  |  | LINEAR | [9 empty] | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | EQ% | [13 empty] | EQ% |  |  |  |  | EQ% |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  |  | LINEAR |  |  |  | EQ% |  |  |  | EQ% |  |  |  | LINEAR |  |  |  |  | LINEAR |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | LINEAR |  |  |  | LINEAR |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | LINEAR |  |  |  |  | LINEAR |  |  |  | EQ% | [6 empty] | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ% |  |  |  |  | EQ% |  |  |  | EQ% |  |  |  | EQ%
40 |  | Leakage Class (ANSI/FCI 70-2) |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV | [6 empty] | IV |  |  |  |  | IV |  |  |  | IV | [6 empty] | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV | [9 empty] | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV | [13 empty] | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV | [6 empty] | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  | IV |  |  |  |  | IV |  |  |  | IV |  |  |  | IV
41
42 | ACTUATOR & POSITIONER | Actuator Type |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM | [6 empty] | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM | [6 empty] | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM | [9 empty] | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM | [13 empty] | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM | [6 empty] | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM |  |  |  | DIAPHRAGM
43 |  | Fail Position |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FO |  |  |  | FC |  |  |  | FC |  |  |  | FO |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | - |  |  |  | FC |  |  |  | - |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC | [6 empty] | FC |  |  |  |  | FC |  |  |  | FC | [6 empty] | FC |  |  |  |  | FC |  |  |  | FO |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FO | [9 empty] | FC |  |  |  |  | FC |  |  |  | FO |  |  |  | FC |  |  |  | FO |  |  |  |  | FO |  |  |  | FC |  |  |  | FC |  |  |  | FO | [13 empty] | FC |  |  |  |  | FO |  |  |  | FC |  |  |  | FO |  |  |  | FC |  |  |  |  | FO |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FO |  |  |  |  | FO |  |  |  | FO |  |  |  | FO |  |  |  | FO |  |  |  |  | FO |  |  |  | FO |  |  |  | FO |  |  |  | FO |  |  |  |  | FO |  |  |  | FC |  |  |  | FO |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FO |  |  |  |  | FO |  |  |  | FC |  |  |  | FC |  |  |  | FO |  |  |  |  | FC |  |  |  | FO | [6 empty] | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  | FC |  |  |  |  | FC |  |  |  | FC |  |  |  | FC
44 |  | Positioner Type |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL | [6 empty] | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL | [6 empty] | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL | [9 empty] | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL | [13 empty] | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL | [6 empty] | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
45 |  | Gauges |  | Bypass | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES | [6 empty] | YES |  |  |  |  | YES |  |  |  | YES | [6 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | [9 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES | [13 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES | [6 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES
46 |  | Signal Input |  | Signal Output | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA | [6 empty] | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA | [6 empty] | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA | [9 empty] | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA | [13 empty] | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA | [6 empty] | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  |  | 4~20 mA |  |  |  | 4~20 mA |  |  |  | 4~20 mA
47 |  | Electrical Conn. |  | Pneumatic Conn. | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  |  |  |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  |  |  |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT | [7 empty] | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT | [10 empty] | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  |  |  |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT
48 |  | Air Supply Pressure |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g | [6 empty] | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g | [6 empty] | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g | [9 empty] | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g | [13 empty] | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g | [6 empty] | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g |  |  |  | 5 kg/cm2g
49 |  | Air Tube & Fittings Material |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS | [9 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS | [13 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS | [6 empty] | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS |  |  |  |  | 316SS |  |  |  | 316SS |  |  |  | 316SS
50 |  | Air Set |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES | [6 empty] | YES |  |  |  |  | YES |  |  |  | YES | [6 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | [9 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES | [13 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES | [6 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | YES
51 |  | Lockup |  | Handwheel | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  |  |  |  | - |  |  | - |  | - |  | - |  | - |  | - |  |  |  |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - | [7 empty] | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - | [10 empty] | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  |  |  |  | - |  |  | YES |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  |  | - |  | - |  | - |  | - |  | - |  | - |  | -
52 |  | Quick Exhaust |  | Volumn Booster
53 |  | Solenoid V/V |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - | [9 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - | [13 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | -
54 |  | Limit Switch |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - | [9 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - | [13 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - | [6 empty] | - |  |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | -
55
56 | PROQ. | Manufacturer
57 |  | Body Model
58 |  | Actuator Model
[6 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [15 empty] | NOTE | [15 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [14 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [13 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [16 empty] | NOTE | [15 empty] | NOTE | [16 empty] | NOTE
[6 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [14 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [14 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [13 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [12 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [14 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor. | [15 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor.
[6 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [14 empty] | 2. | Stainless steel name plate shall be supplied. | [14 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [13 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [12 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied. | [14 empty] | 2. | Stainless steel name plate shall be supplied. | [15 empty] | 2. | Stainless steel name plate shall be supplied.
[40 empty] | 3. | Ice formation may be possibe on FV-1226. | [83 empty] | 3. | FV-1358 Outlet Condition (Flash% = 10.119) | [48 empty] | 3. | LV-1112 Outlet Condition (Flash% = 0.34) | [14 empty] | 3. | LV-1210 Outlet Condition (Flash% = 29.23) | [197 empty] | 3. | Mechanical stop for TV-1383 shall be provided to assure min. flow of 10%. | [32 empty] | 3. | Mechanical stop for TV-1397 shall be provided to assure min. flow of 10%. | [31 empty] | 3. | Volume tank shall be provided for HV-1119 & HV-1146
[126 empty] | Vapor = MW : 46.78 Viscosity : 0.01 Cp/Cv : 1.12 | [49 empty] | Vapor = MW : 67.0, Viscosity : 0.019, Cp/Cv : 1.22 | Vapor = MW : 67.0, Viscosity : 0.019, Cp/Cv : 1.22 | [14 empty] | Vapor = MW : 58.71 Viscosity : 0.01 Cp/Cv : 1.13
[126 empty] | Liquid = Density : 744.0 Viscosity : 0.423 | [49 empty] | Liquid = Density : 828.7, Viscosity : 0.217 | Liquid = Density : 828.7, Viscosity : 0.217 | [14 empty] | Liquid = Density : 648.9 Viscosity : 0.18
[175 empty] | 4. | LV-1147 Outlet Condition (Flash% = 100) | [14 empty] | 4. | LV-1220 Outlet Condition (Flash% = 100)
[176 empty] | Vapor = MW : 43.9, Viscosity : 0.009, Cp/Cv : 1.14 | [15 empty] | Vapor = MW : 43.3, Viscosity : 0.009, Cp/Cv : 1.14
Ice formation may be possible on LV-1220.

## Angle Valve
[5 empty] | DATA SHEET | [11 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  | : M0556 |  | CONTROL VALVE (ANGLE) | [11 empty] | DS-IN-F-030
| PROJECT NAME |  | : IPA 50KTA Exp. | [13 empty] | REV. NO.
| LOCATION |  | : Yeosu, Korea | [13 empty] | A
1 | GENERAL | Tag No. |  |  | LV-1150 |  |  |  |  | LV-1157
2 |  | P&ID No. |  |  | D-1-IPA-1003 |  |  |  |  | D-1-IPA-1003
3 |  | Service |  |  | FC-150 FEED INLET |  |  |  |  | FC-155 FEED INLET
4 |  | Line Class |  |  | BB59C1 |  |  |  |  | BB57C1
5 |  | Line Size |  | Line Schedule | 4" |  |  |  |  | 3"
6 |  | Nace Requirement
7 |  | Enclosure Class |  |  | Ex d IIB T4, IP56 |  |  |  |  | Ex d IIB T4, IP56
8
9 | SERVICE CONDITION | Fluid |  |  | PDI |  |  |  |  | PDI
10 |  | Flow Rate Unit |  | State | m3/h |  |  |  | L | m3/h |  |  | L
11 |  |  |  |  | MAX |  | NOR |  | MIN | MAX | NOR |  | MIN | MAX | NOR | MIN | MAX | NOR | MIN
12 |  | Flow Rate |  |  | 78.6276 |  | 65.523 |  | - | 76.62 | 63.85 |  | -
13 |  | Inlet Pressure |  | (kg/cm2g) | - |  | 31.6 |  | - | - | 16.8 |  | -
14 |  | Pressure Drop |  | (kg/cm2) |  |  | 14.5 |  |  |  | 16
15 |  | Temperature |  | (deg C) | - |  | 94 |  | - | - | 93.03 |  | -
16 |  | Travel |  | (%)
17 |  | Max. Allowable Sound Level |  |  | 85 dBA |  |  |  |  | 85 dBA
18 |  | Calculated Cv |  |  | * |  |  |  |  | *
19 |  | Selected Valve Cv |  |  | * |  |  |  |  | *
20 |  | Shut-Off ΔP |  | (kg/cm2) | 55 |  |  |  |  | 20
21 |  | Design Press. |  | (kg/cm2g) | 55 |  |  |  |  | 20
22 |  | Design Temp. |  | (deg C) | 150 |  |  |  |  | 140
23 |  | Vapor Press. |  | (kg/cm2) | 29.11 |  |  |  |  | 17.83
24 |  | Critical Press. |  | (kg/cm2) | - |  |  |  |  | -
25 |  | S.G. @ Op |  | Density @ Op |  |  |  | 855.62 |  |  |  | 848.7
26 |  | Viscosity @ Op. |  | Molcular Mass | 0.289 |  |  | - |  | 0.25 |  | -
27 |  | Cp/Cv |  | Comp. Factor | - |  |  | - |  | - |  | -
28 | BODY & TRIM | Type of Body |  |  | ANGLE |  |  |  |  | ANGLE
29 |  | Body Size |  | Port Size | * |  |  | * |  | * |  | *
30 |  | Connection Rating (ANSI) |  |  | 600# RF |  |  |  |  | 300# RF
31 |  | Flange Face Finish |  |  | 125 ~ 250 AARH |  |  |  |  | 125 ~ 250 AARH
32 |  |  |  | Body | A216 WCB |  |  |  |  | A216 WCB
33 |  |  |  | Plug / Ball / Disk | 316SS+ST |  |  |  |  | 316SS+ST
34 |  | Material |  | Seat | 316SS+ST |  |  |  |  | 316SS+ST
35 |  |  |  | Stem | 316SS |  |  |  |  | 316SS
36 |  |  |  | Guide / Cage | 316SS |  |  |  |  | 316SS
37 |  |  |  | Packing | PTFE |  |  |  |  | PTFE
38 |  | Type of Bonnet |  |  | STANDARD |  |  |  |  | STANDARD
39 |  | Characteristic |  |  | LINEAR |  |  |  |  | LINEAR
40 |  | Leakage Class (ANSI/FCI 70-2) |  |  | IV |  |  |  |  | IV
41
42 | ACTUATOR & POSITIONER | Actuator Type |  |  | DIAPHRAGM |  |  |  |  | DIAPHRAGM
43 |  | Fail Position |  |  | FC |  |  |  |  | FC
44 |  | Positioner Type |  |  | CONVENTIONAL |  |  |  |  | CONVENTIONAL
45 |  | Gauges |  | Bypass | YES |  |  |  |  | YES
46 |  | Signal Input |  | Signal Output | 4~20 mA |  |  |  |  | 4~20 mA
47 |  | Electrical Conn. |  | Pneumatic Conn. | 1/2" NPT |  |  | 1/4" NPT |  | 1/2" NPT |  | 1/4" NPT
48 |  | Air Supply Pressure |  |  | 5 kg/cm2g |  |  |  |  | 5 kg/cm2g
49 |  | Air Tube & Fittings Material |  |  | 316SS |  |  |  |  | 316SS
50 |  | Air Set |  |  | YES |  |  |  |  | YES
51 |  | Lockup |  | Handwheel | - |  |  | - |  | - |  | -
52 |  | Quick Exhaust |  | Volumn Booster
53 |  | Solenoid V/V |  |  | - |  |  |  |  | -
54 |  | Limit Switch |  |  | - |  |  |  |  | -
55
56 | PROQ. | Manufacturer
57 |  | Body Model
58 |  | Actuator Model
NOTE
[6 empty] | 1. | " * " Marked Items shall be specified or recommended by Vendor.
[6 empty] | 2. | Stainless steel name plate shall be supplied.
[6 empty] | 3. | LV-1150 Outlet Condition (Flash% = 3)
Vapor = MW : 43.8, Viscosity : 0.011, Cp/Cv : 1.29
Liquid = Density : 863.8, Viscosity : 0.298
[6 empty] | 4. | LV-1157 Outlet Condition (Flash% = 4)
Vapor = MW : 46.0, Viscosity : 0.010, Cp/Cv : 1.15
Liquid = Density : 890.2, Viscosity : 0.349