## Cover
[6 empty] | DATA SHEET | [5 empty] | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  |  | : M0556 |  | CCTV | [5 empty] | DS-IN-F-041
| PROJECT NAME |  |  | : IPA 50KTA Exp. | [7 empty] | REV. NO.
| LOCATION |  |  | : Yeosu, Korea | [7 empty] | A
IPA
| CLIENT |  | LG Chem Ltd.
| PROJECT |  | IPA 50 KTA Expansion
| LOCATION |  | Yeosu, Korea
UNIT
DATA SHEET
FOR
CCTV
SERVEONE |  |  |  |  | SERVEONE CONFIDENTIAL INFORMATION: The drawings, designs, ideas, specifications and information contained in this document constitute
confidential information belonging to SERVEONE. Neither this document nor its contents may be used for any purpose or disclosed in any manner
CONSTRUCTION BUSINESS UNIT |  |  |  |  | without the prior written consent of SERVEONE. Reproduction of this document without the prior written consent of SERVEONE or LG Chem.,Ltd.
is prohibited. Any authorized reproduction of this document, or any part thereof, including vendors' shop drawings, shall incorporate this notice."
A |  | AUG. 30. '18 |  |  | FOR QUOTATION |  | J.H Jung |  | C.M Lee | K.Y Noh |  |  | H.D Yoon
Rev. |  | Date |  |  | Description |  | Prepared |  | Checked | Approved |  |  | Authorized
JOB NO. |  |  |  |  | DEPARTMENT |  |  | DOCUMENT NO. |  |  | ISSUE DATE
M0556 |  |  |  |  | E&I (INSTRUMENT) |  |  | DS-IN-F-041 |  |  | 2018.08.30

## GENERAL
|  |  | DATA SHEET | CLIENT
LG Chem
DOC. NO.
| JOB NO. | : M0556 | CCTV (PROCESS MONITORING) | DS-IN-F-041
| PROJECT NAME | : IPA 50KTA Exp. |  | REV. NO.
| LOCATION | : Yeosu, Korea |  | A
1 | GENERAL NOTES
2
3 | 1. Instrument equipment vendors shall furnish the items below marked with "Instrument Tag Number" and "Requisition Number"
4 | a) Specification sheets with Instrument Tag Number
5 | b) System Block Diagram
6 | c) Vendor Catalog
7 | d) Spare parts listing and option pricing for 1-Year operation.
8 | e) Material List for Construction
9 | f) KOSHA or KTL certificate for explosion proof
10
11 | 2. All equipment shall comply with all applicable nation and local laws, regulations and standards in addition to those listed above.
12
13 | 3. All materials for CCTV works, design drawings and installation practices shall be subject to prior approval by Purchaser
14
15 | 4. The Vendor's scope of supply and work shall be as follows:
16 | a) Complete set of hardware which includes "system staging"
17 | b) Communication interfaces and connection with other system such as computer
18 | c) Calibration equipment and tools
19 | d) Documents (Including Layout for CCTV System Drawing)
20 | e) All installation materials
21 | f) Installation of system cable, signal cable, fiber optic cable and power cable among the equipment at job site.
22
23 | 5. Remote CCTV control Unit : 1 Set
24 | a) Facilities for controlling all camera functions including pan, tilt zoom, auto scan, focus and wash/wipe shall be incorporated by
25 | Vendor in Remote Control Units with additional cable extension Controlling functions.
26 | a) The operator shall have the facility to select and deselect cameras from auto scan and to assign one camera to any one monitor.
27 | b) The unit shall be capable of switching the output from any camera to any monitor in the system.
28 | c) The unit shall be suitable for arranging the output from up to for cameras to be displayed simultaneously on a single monitor by
29 | splitting the screen display into four sections
30
31 | 6. Color video monitor : 2 sets
32 | Color monitors shall be a LED screen as minimum size 65 inches and 24 inches
33
34 | 7. Recorder with Control system : 1 Set (for Process Monitor & Electric Equipments)
35 | a) This is all-in-one solution concept which is including various network operation(Live, Control, Recording, Playback, Downloading, Edit)
36 | b) This facilities directly operate the CCTV same as control unit and transfer signal to video monitor.
37 | c) This facilities should memorize that record of during 1 Year each camera
38
39 | 8. Inspection and Tests
40 | a) The inspection and tests shall be conducted in accordance with Manufacturer's standard and practices with the Purchaser's approval.
41 | b) The Purchaser reserves the right to witness the shop test and inspect the commodity in the Vendor's Factory.
42
43 | 9. The latest edition of the following publications shall be applicable
44 | a) International Electrotechnical Commission (IEC)
45 | b) American Narional Standards Institute (ANSI)
46 | c) Institute If Electrical and Electronics Engineers (IEEE)
47 | d) National Elecal Code (NEC)
48 | e) National Electrical Manufacturers Association (NEMA)
49 | f) Korea Standard (KS)
50
51 | 10. Others
52 | a) All electrical connection holes shall be NPT threaded.
53 | b) Vendor shall attach a permanent stainless steel tag inscribed to each camera, receiving unit and monitor
54 | c) Even if not directly specified in this sheet, vendor shall have the obligation to supply all requisite accessories to make
55 | a fully operational system.
56
57
58
NOTE

## DATA SHEET
|  |  |  | DATA SHEET | CLIENT
LG Chem
DOC. NO.
| JOB NO. |  | : M0556 | CCTV | DS-IN-F-041
| PROJECT NAME |  | : IPA 50KTA Exp. |  | REV. NO.
| LOCATION |  | : Yeosu, Korea |  | A
1 | GENERAL | Tag Name |  | CCTV-1002, CCTV-1003, CCTV-1004
2 |  | Type |  | 방폭 회전형
3 |  | P&ID No.
4 |  | Service |  | Recycle Compressor 1 ea, Process Area(대각선 방향) 2ea
5 |  | Compatibility |  | 방재실 VMS 시스템 호환기종
6
7
8 | COLOR CAMERA | Image Sensor |  | 1/4" Processive Scan CMOS
9 |  | Max. Resolution |  | Full-HD 1920*1080 (2MP)
10 |  | Image |  | Corridor Format, mirroning of images
11 |  | Focus |  | Auto
12 |  | Zoom |  | 광학 10배줌/디지털 12배줌
13 |  | 영상압축 |  | H.264, Motion JPEG
14 |  | 초당프레임수 |  | 30 fps (1080p)
15 |  | PTZ 지원 |  | Preset positions, Guard tour, RS-485, RS-422
16 |  | 오디오지원 |  | 양방향
17 |  | 수평시야각 |  | 5.4º~50º
18 |  | Day & Night |  | Auto
19 |  | 지능형 |  | 모션디텍션, 엑티브 알람 펨퍼링. Gatekeeper
20 |  | 보안 |  | 다중접속보안, IP필터링 IEEE802.1X, HTTPS암호화
21 |  | Quantity |  | 3 Sets
22
23
24
25 | CAMERA HOUSING | Enclosure Class |  | Exd IIB T4, IP56 MIN.
26 |  | Wiper |  | YES
27 |  | Cooling Fan/Heater
28 |  | Air Purge Set
29 |  | Window |  | Tempered Glass
30 |  | Quantity |  | 3 Sets
31
32
33
34 | ADJUSTABLE ANGLE (DRIVER) | Enclosure Class |  | Exd IIB T4, IP56 MIN.
35 |  | Horizontal(Pan) |  | 0º ~ 355º ±5º
36 |  | Vertical(Tilt) |  | -90º ~ +90º
37 |  | Power Supply |  | AC 110V 60Hz
38 |  | Material |  | STS-304
39 |  | Quantity |  | 3 Sets
40
41
42
43
44 | RECEIVER UNIT | Enclosure Class |  | Exd IIB T4, IP56 MIN.
45 |  | Communication |  | RS-485, 232
46 |  | Power Supply |  | AC 110V 60Hz
47 |  | Material |  | STS-304
48 |  | Quantity |  | 3 Sets
49
50
51
52 | PROQ. | Manufacturer
53 |  | Model
54
NOTE
1 | GENERAL | Tag Name |  | CCTV-1001
2 |  | Type |  | 비방폭 회전형
3 |  | P&ID No.
4 |  | Service |  | Process Area on MCC 1ea
5 |  | Compatibility |  | 방재실 VMS 시스템 호환기종
6
7
8 | COLOR CAMERA | Image Sensor |  | 1/4" Processive Scan CMOS
9 |  | Max. Resolution |  | Full-HD 1920*1080 (2MP)
10 |  | Image |  | Corridor Format, mirroning of images
11 |  | Focus |  | Auto
12 |  | Zoom |  | 광학 10배줌/디지털 12배줌
13 |  | 영상압축 |  | H.264, Motion JPEG
14 |  | 초당프레임수 |  | 30 fps (1080p)
15 |  | PTZ 지원 |  | Preset positions, Guard tour, RS-485, RS-422
16 |  | 오디오지원 |  | 양방향
17 |  | 수평시야각 |  | 5.4º~50º
18 |  | Day & Night |  | Auto
19 |  | 지능형 |  | 모션디텍션, 엑티브 알람 펨퍼링. Gatekeeper
20 |  | 보안 |  | 다중접속보안, IP필터링 IEEE802.1X, HTTPS암호화
21 |  | Quantity |  | 1 Set
22
23
24
25 | CAMERA HOUSING | Enclosure Class
26 |  | Wiper
27 |  | Cooling Fan/Heater
28 |  | Air Purge Set
29 |  | Window
30 |  | Quantity
31
32
33
34 | ADJUSTABLE ANGLE (DRIVER) | Enclosure Class |  | IP56 MIN.
35 |  | Horizontal(Pan) |  | 0º ~ 355º ±5º
36 |  | Vertical(Tilt) |  | -90º ~ +90º
37 |  | Power Supply |  | AC 110V 60Hz
38 |  | Material |  | STS-304
39 |  | Quantity |  | 1 Set
40
41
42
43
44 | RECEIVER UNIT | Enclosure Class |  | IP56 MIN.
45 |  | Communication |  | RS-485, 232
46 |  | Power Supply |  | AC 110V 60Hz
47 |  | Material |  | STS-304
48 |  | Quantity |  | 1 Set
49
50
51
52 | PROQ. | Manufacturer
53 |  | Model
54
NOTE
1 | GENERAL | Tag Name |  | CCTV-1005
2 |  | Type |  | 비방폭 고정형
3 |  | P&ID No.
4 |  | Service |  | 우수집수조
5 |  | Compatibility |  | 방재실 VMS 시스템 호환기종
6
7
8 | COLOR CAMERA | Image Sensor |  | 1/4" Processive Scan CMOS
9 |  | Max. Resolution |  | Full-HD 1920*1080 (2MP)
10 |  | Image |  | Corridor Format, mirroning of images
11 |  | Focus |  | Auto
12 |  | Zoom |  | 광학 10배줌/디지털 12배줌
13 |  | 영상압축 |  | H.264, Motion JPEG
14 |  | 초당프레임수 |  | 30 fps (1080p)
15 |  | PTZ 지원 |  | N/A
16 |  | 오디오지원 |  | 양방향
17 |  | 수평시야각 |  | 5.4º~50º
18 |  | Day & Night |  | Auto
19 |  | 지능형 |  | 모션디텍션, 엑티브 알람 탬퍼링. Gatekeeper
20 |  | 보안 |  | 다중접속보안, IP필터링 IEEE802.1X, HTTPS암호화
21 |  | Quantity |  | 1 Set
22
23
24
25 | CAMERA HOUSING | Enclosure Class |  | IP56 MIN.
26 |  | Wiper
27 |  | Cooling Fan/Heater
28 |  | Air Purge Set
29 |  | Window
30 |  | Quantity
31
32
33
34 | ADJUSTABLE ANGLE (DRIVER) | Enclosure Class
35 |  | Horizontal(Pan)
36 |  | Vertical(Tilt)
37 |  | Power Supply
38 |  | Material
39 |  | Quantity
40
41
42
43
44 | RECEIVER UNIT | Enclosure Class
45 |  | Communication
46 |  | Power Supply
47 |  | Material
48 |  | Quantity
49
50
51
52 | PROQ. | Manufacturer
53 |  | Model
54
NOTE