## Flow
Rev | Name | Case | Old Tag Name | Logically deleted from the project | Inst_Type_Code | Seq No | Suffix | Qty | P&ID No | Service | Inst Type Desc | Line Size | Plant Connection (Text) | Line Spec | Fluid Code | Fluid Name | Phase | OP Max | OP Nor | OP Min | OP UOM | OT Max | OT Nor | OT Min | OT UOM | DP (Int) | DP (Int) UOM | DP (FV) | DT Hot | DT Cold | DT UOM | Flow Rate Max | Flow Rate Nor | Flow Rate Min | Flow Rate UOM | Pressure Loss Maximum | Pressure Loss Normal | Press Loss UOM | Density | Density UOM | Viscosity | Viscosity UOM | MW | CpCv | Comp. Z | Critical_Press | Critical_Press_UOM | Vapor_Press | Vapor_Press_UOM | Flash Percent | UOM for Flash Percent | Remarks-PS
A | FT-3111C |  | FT-3111A | FALSE | FT | 3111 | A | 1 | B-1-3111A | EE TO HE-3101A |  | 2" |  | C27 | EE |  | V |  | 1 |  | BARG |  | 15 | -10 | deg C | 34.32 | BARG | - | 60 | -45 | deg C | 173 | 115 |  | Nm3/hr |  | 0.19613 | BAR |  |  | 0.01 | cP | 28.05 | 1.296 | 0.954
A | FT-3111D |  | FT-3111B | FALSE | FT | 3111 | B | 1 | B-1-3111B | EE TO HE-3101B |  | 2" |  | C27 | EE |  | V |  | 2 |  | BARG |  | 15 | -10 | deg C | 34.32 | BARG | - | 60 | -45 | deg C | 173 | 115 |  | Nm3/hr |  | 0.19613 | BAR |  |  | 0.01 | cP | 28.05 | 1.296 | 0.954
A | FT-3112A |  | FT-3112C | FALSE | FT | 3112 | A | 1 | B-1-3111A | SL TO HE-3101A |  | 1" |  | A21 | SL |  | S |  | 3 |  | BARG |  | 152 |  | deg C | 9.81 | BARG | F.V | 175 |  | deg C | 25.65 | 14.00 |  | kg/hr |  | 0.19613 | BAR |  |  | 0.01 | cP | 18.02 | 1.350 | 0.970
A | FT-3112B |  |  | FALSE | FT | 3112 | B | 1 | B-1-3111B | SL TO HE-3101B |  | 1" |  | A21 | SL |  | S |  | 10 |  | BARG |  | 152 |  | deg C | 9.81 | BARG | F.V | 175 |  | deg C | 25.65 | 14.00 |  | kg/hr |  | 0.19613 | BAR |  |  | 0.01 | cP | 18.02 | 1.350 | 0.970
F | FT-3121A |  |  | FALSE | FT | 3121 | A | 1 | B-1-3111A | NL TO EH-3102A |  | 4" |  | A50 | NL |  | G |  | 1.96 |  | BARG | 150 | 25 |  | deg C | 3.43 | BARG | - | 400 |  | deg C | 435 | 290 |  | Nm3/hr |  | 0.19613 | BAR |  |  | 0.02 | cP | 28.01 | 1.404 | 0.999 | [6 empty] | 60% 3D MODEL COMMENT에 따라 변경
F | FT-3121B |  |  | FALSE | FT | 3121 | B | 1 | B-1-3111B | NL TO EH-3102B |  | 4" |  | A50 | NL |  | G |  | 1.96 |  | BARG | 150 | 25 |  | deg C | 3.43 | BARG | - | 400 |  | deg C | 435 | 290 |  | Nm3/hr |  | 0.19613 | BAR |  |  | 0.02 | cP | 28.01 | 1.404 | 0.999 | [6 empty] | 60% 3D MODEL COMMENT에 따라 변경
F | FT-3301A |  |  | FALSE | FT | 3301 | A | 1 | B-1-3312A | NL TO EH-3301A | MASS FLOWMETER | 2" |  | A50 | NL |  | G |  | 25 |  | mmH2O |  | AMB |  | deg C | 3.43 | BARG | - | 130 |  | deg C | 50.00 | 40.00 |  | Nm3/hr |  | MIN. | BAR |  |  | 0.02 | cP | 28.01 | 1.404 | 0.999 | [6 empty] | Thermal Mass Flowmeter Need to Electric Jacket Heater Vendor Confirm OP PRESSURE UNIT: mmH2O
F | FT-3301B | CASE1 |  | FALSE | FT | 3301 | B | 1 | B-1-3312B | NL TO EH-3301B | MASS FLOWMETER | 2" |  | B50 | NL |  | G |  | 25 |  | mmH2O |  | AMB |  | deg C | 3.43 | BARG | - | 130 |  | deg C | 50.00 | 40.00 |  | Nm3/hr |  | MIN. | BAR |  |  | 0.02 | cP | 28.01 | 1.404 | 0.999 | [6 empty] | Thermal Mass Flowmeter Need to Electric Jacket Heater Vendor Confirm OP PRESSURE UNIT: mmH2O
F | FT-3301B | CASE2 |  | FALSE | FT | 3301 | B | 1 | B-1-3312B | NL TO EH-3301B | MASS FLOWMETER | 2" |  | B50 | NL |  | G |  | 25 |  | mmH2O |  | AMB |  | deg C | 3.43 | BARG | - | 130 |  | deg C | 50.00 | 40.00 |  | Nm3/hr |  | MIN. | BAR |  |  | 0.02 | cP | 28.01 | 1.404 | 0.999 | [6 empty] | Thermal Mass Flowmeter Need to Electric Jacket Heater Vendor Confirm OP PRESSURE UNIT: mmH2O
C | FT-3311A |  |  | TRUE | FT | 3311 | A | 1 | B-1-3312A | HEATED NG TO RE-3301A SIDE N1A~D |  | 3" |  | B50 | NG |  | G | 6.86 | 6.18 |  | BARG |  | 250 |  | deg C | 9.71 | BARG | F.V | 400 |  | deg C | 300 | 125 | 30.00 | Nm3/hr |  | 0.19613 | BAR |  |  | 0.03 | cP | 28.01 | 1.380 | 1.002 | [6 empty] | Flow Range 300~30 Nm3/hr Need to Check by Vendor Min. Flow Value
C | FT-3311C |  |  | FALSE | FT | 3311 | B | 1 | B-1-3312B | HEATED NG TO RE-3301B SIDE N1A~D |  | 3" |  | B50 | NG |  | G | 6.86 | 6.18 |  | BARG |  | 250 |  | deg C | 9.71 | BARG | F.V | 400 |  | deg C | 300 | 125 | 30.00 | Nm3/hr |  | 0.19613 | BAR |  |  | 0.03 | cP | 28.01 | 1.380 | 1.002 | [6 empty] | Flow Range 300~30 Nm3/hr Need to Check by Vendor Min. Flow Value

## Level
Rev | Name | Case | Old Tag Name | Logically deleted from the project | Inst_Type_Code | Seq No | Suffix | Qty | P&ID No | Service | Inst Type Desc | Line Size | Plant Connection (Text) | Line Spec | Fluid Code | Fluid Name | Phase | OP Max | OP Nor | OP Min | OP UOM | OT Max | OT Nor | OT Min | OT UOM | DP (Int) | DP (Int) UOM | DP (FV) | DT Hot | DT Cold | DT UOM | Density | Density UOM | Viscosity | Viscosity UOM | Conductivity | Conductivity UOM | Remarks-PS
G | LG-2721 |  |  | FALSE | LG | 2721 |  | 1 | B-1-2714-1 | OIL TANK |  |  | OIL TANK |  | OIL |  | L |  | HOLD |  | BARG |  | HOLD |  | degC | HOLD | BARG |  | HOLD |  | degC |  | kg/m3 |  | cP |  | S/m
A | LG-3611A |  |  | FALSE | LG | 3611 | A | 1 | B-1-3611 | DV-3611A |  |  | DV-3611A |  | WF |  | L |  |  |  | BARG |  |  |  | degC |  | BARG |  |  |  | degC |  | kg/m3 |  | cP |  | S/m
F | LS-3741B |  |  | FALSE | LS | 3741 | B | 1 | B-1-3740 | HP-3741 |  |  | HP-3741 |  | CT |  | SD |  |  |  | BARG |  |  |  | degC |  | BARG |  |  |  | degC |  | kg/m3 |  | cP |  | S/m
B | LS-3742 |  |  | FALSE | LS | 3742 |  | 1 | B-1-3741 | DC-3741 |  |  | DC-3741 |  | DVG |  | SD/G |  | 1 |  | BARG |  | 25 |  | degC | FW+0.29 | BARG |  | 60 |  | degC |  | kg/m3 |  | cP |  | S/m
B | LS-3811 |  |  | FALSE | LS | 3811 |  | 1 | B-1-3805 | DC-3801 |  |  | DC-3801 |  | DVG |  | SD/G |  | -0.39 | -0.45 | BARG |  | 25 |  | degC | F.W+0.29 | BARG |  | 60 |  | degC |  | kg/m3 |  | cP |  | S/m
F | LT-3501A |  | LT-3501D | FALSE | LT | 3501 | A | 1 | B-1-3512 | TW-3501A |  |  | TW-3501A |  | WF |  | L |  | 0.10 |  | BARG |  | 25 |  | degC | F.W+0.10 | BARG |  | 100 |  | degC |  | kg/m3 | 0.89 | cP |  | S/m
F | LT-3501C |  | LT-3510B | FALSE | LT | 3501 | C | 1 | B-1-3512 | TW-3501B |  |  | TW-3501B |  | WF |  | L |  | 0.10 |  | BARG |  | 25 |  | degC | F.W+0.10 | BARG |  | 100 |  | degC |  | kg/m3 | 0.89 | cP |  | S/m
F | LT-3502A |  |  | FALSE | LT | 3502 | A | 1 | B-1-3511A | DV-3502A |  |  | DV-3502A |  | CT |  | SD/G | 1.96 | 0.20 |  | BARG |  | 30 |  | degC | 3.43 | BARG |  | 100 |  | degC |  | kg/m3 |  | cP |  | S/m
F | LT-3502B |  |  | FALSE | LT | 3502 | B | 1 | B-1-3511B | DV-3502B |  |  | DV-3502B |  | CT |  | SD/G | 1.96 | 0.20 |  | BARG |  | 30 |  | degC | 3.43 | BARG |  | 100 |  | degC |  | kg/m3 |  | cP |  | S/m
F | LT-3503 |  |  | FALSE | LT | 3503 |  | 1 | B-1-3512 | TW-3503 |  |  | TW-3503 |  | WF |  | L |  | 0.00 |  | BARG |  | 25 |  | degC | F.W+500 | mmH2O |  | 100 |  | degC |  | kg/m3 | 0.89 | cP |  | S/m

## Press
Rev | Name | Case | Old Tag Name | Logically deleted from the project | Inst_Type_Code | Seq No | Suffix | Qty | P&ID No | Service | Inst Type Desc | Line Size | Line Spec | Plant Connection (Text) | Fluid Code | Fluid Name | Phase | OP Max | OP Nor | OP Min | OP UOM | OT Max | OT Nor | OT Min | OT UOM | DP (Int) | DP (Int) UOM | DP (FV) | DT Hot | DT Cold | DT UOM | Pressure Loss Maximum | Pressure Loss Normal | Press Loss UOM | Remarks-PS
G | PDG-2721E |  |  | FALSE | PDG | 2721 | E | 1 | B-1-2714 | BF-2721E |  |  |  | BF-2721E | DVG |  | SD/G |  | ATM |  | BARG |  | AMB |  | degC | 0.30 | BARG |  | 60 |  | degC
A | PDT-3301A |  |  | FALSE | PDT | 3301 | A | 1 | B-1-3311A | BF-3301A |  |  |  | BF-3301A | DVG |  | SD/G |  | ATM |  | BARG |  | AMB |  | degC | F.W | BARG |  | 175 |  | degC |  | 5 | mBAR
A | PG-3111A |  |  | FALSE | PG | 3111 | A | 1 | B-1-3111A | SL TO HE-3101A |  | 1" | A21 |  | SL |  | S |  | 3.92 |  | BARG |  | 152 |  | degC | 9.81 | BARG | F.V | 175 |  | degC
A | PT-3101A |  |  | FALSE | PT | 3101 | A | 1 | B-1-3111A | DV-3101A |  | 2" | B55 |  | MG |  | G | 0.39 | 0.20 | 0.10 | BARG | 500 | 300 |  | degC | 3.43 | BARG | F.V | 650 |  | degC
A | PT-3101B |  |  | FALSE | PT | 3101 | B | 1 | B-1-3111B | DV-3101B |  | 2" | B55 |  | MG |  | G | 0.39 | 0.20 | 0.10 | BARG | 500 | 300 |  | degC | 3.43 | BARG | F.V | 650 |  | degC
A | PT-3113A |  |  | FALSE | PT | 3113 | A | 1 | B-1-3111A | EE TO HE-3101A |  | 2" | A26 |  | EE |  | V |  | 3.92 |  | BARG |  | 15 | -10 | degC | 34.32 | BARG |  | 60 | -45 | degC
A | PT-3113B |  |  | FALSE | PT | 3113 | B | 1 | B-1-3111B | EE TO HE-3101B |  | 2" | C27 |  | EE |  | V |  | 3.92 |  | BARG |  | 15 | -10 | degC | 34.32 | BARG |  | 60 | -45 | degC
A | PT-3114A |  |  | FALSE | PT | 3114 | A | 1 | B-1-3111A | EE TO DV-3101A |  | 3" | A26 |  | EE |  | V | 0.39 | 0.20 |  | BARG |  | 120 |  | degC | 3.43 | BARG | F.V | 200 |  | degC
A | PT-3114B |  |  | FALSE | PT | 3114 | B | 1 | B-1-3111B | EE TO DV-3101B |  | 3" | A26 |  | EE |  | V | 0.39 | 0.20 |  | BARG |  | 120 |  | degC | 3.43 | BARG | F.V | 200 |  | degC
F | PT-3121A |  |  | FALSE | PT | 3121 | A | 1 | B-1-3111A | NL TO EH-3102A |  | 4" | A50 |  | NL |  | G |  | 1.96 |  | BARG | 150 | 25 |  | degC | 3.43 | BARG |  | 400 |  | degC

## Temp
Rev | Name | Case | Old Tag Name | Logically deleted from the project | Inst_Type_Code | Seq No | Suffix | Qty | P&ID No | Service | Inst Type Desc | Line Size | Line Spec | Plant Connection (Text) | Fluid Code | Fluid Name | Phase | OP Max | OP Nor | OP Min | OP UOM | OT Max | OT Nor | OT Min | OT UOM | DP (Int) | DP (Int) UOM | DP (FV) | DT Hot | DT Cold | DT UOM | Velocity | Velocity UOM | Density | Density UOM | Viscosity | Viscosity UOM | MW | CpCv | Comp. Z | Remarks-PS
A | TG-3316A |  |  | FALSE | TG | 3316 | A | 1 | B-1-3312A | HEATED NG TO RE-3301A SIDE |  | 4" | B50 |  | NG |  | G | 6.86 | 6.18 |  | BARG | 300 | 250 |  | degC | 9.71 | BARG | F.V | 400 |  | degC |  | m/s |  | kg/m3 | 0.03 | cP | 28.01 | 1.380 | 1.003
A | TG-3316B |  |  | FALSE | TG | 3316 | B | 1 | B-1-3312B | HEATED NG TO RE-3301B SIDE |  | 4" | B50 |  | NG |  | G | 6.86 | 6.18 |  | BARG | 300 | 250 |  | degC | 9.71 | BARG | F.V | 400 |  | degC |  | m/s |  | kg/m3 | 0.03 | cP | 28.01 | 1.380 | 1.003
A | TT-3101A |  |  | FALSE | TT | 3101 | A | 1 | B-1-3111A | MG TO RE-3301A |  | 6" | B55 |  | MG |  | G | 0.39 | 0.20 | 0.10 | BARG | 500 | 300 |  | degC | 3.43 | BARG | F.V | 650 |  | degC |  | m/s |  | kg/m3 | 0.02 | cP | 28.02 | 1.254 | 1.000
A | TT-3101C |  | TT-3101B | FALSE | TT | 3101 | B | 1 | B-1-3111B | MG TO RE-3301B |  | 6" | B55 |  | MG |  | G | 0.39 | 0.20 | 0.10 | BARG | 500 | 300 |  | degC | 3.43 | BARG | F.V | 650 |  | degC |  | m/s |  | kg/m3 | 0.02 | cP | 28.02 | 1.254 | 1.000
A | TT-3102A |  |  | FALSE | TT | 3102 | A | 1 | B-1-3111A | NL TO DV-3101A |  | 6" | B55 |  | NL |  | G | 0.39 | 0.20 |  | BARG |  | 560 |  | degC | 3.43 | BARG | F.V | 650 |  | degC |  | m/s |  | kg/m3 | 0.04 | cP | 28.01 | 1.354 | 1.001
A | TT-3102B |  |  | TRUE | TT | 3102 | B | 1 | B-1-3111B | NL TO DV-3101B |  | 8" | B55 |  | NL |  | G | 0.39 | 0.20 |  | BARG |  | 560 |  | degC | 3.43 | BARG | F.V | 650 |  | degC |  | m/s |  | kg/m3 | 0.04 | cP | 28.01 | 1.354 | 1.001
F | TT-3103A |  |  | FALSE | TT | 3103 | A | 1 | B-1-3111A | NL TO EH-3102A |  | 6" | A50 |  | NL |  | G |  | 0.39 |  | BARG | 370 | 250 |  | degC | 3.43 | BARG | F.V | 400 |  | degC |  | m/s |  | kg/m3 | 0.03 | cP | 28.01 | 1.378 | 1.001
F | TT-3103B |  |  | FALSE | TT | 3103 | B | 1 | B-1-3111B | NL TO EH-3102B |  | 6" | A50 |  | NL |  | G |  | 0.39 |  | BARG | 370 | 250 |  | degC | 3.43 | BARG | F.V | 400 |  | degC |  | m/s |  | kg/m3 | 0.03 | cP | 28.01 | 1.378 | 1.001
F | TT-3103C |  |  | FALSE | TT | 3103 | C | 1 | B-1-3111B | NL TO EH-3102B |  | 6" | A50 |  | NL |  | G |  | 0.39 |  | BARG | 370 | 250 |  | degC | 3.43 | BARG | F.V | 400 |  | degC |  | m/s |  | kg/m3 | 0.03 | cP | 28.01 | 1.378 | 1.001
A | TT-3104A |  |  | FALSE | TT | 3104 | A | 1 | B-1-3111A | EH-3102A |  |  |  |  | NL |  | G |  | 0.39 |  | BARG |  | 560 | AMB | degC | 3.43 | BARG | F.V | 650 |  | degC |  | m/s |  | kg/m3 |  | cP
A | TT-3104B |  |  | FALSE | TT | 3104 | B | 1 | B-1-3111A | EH-3102A |  |  |  |  | NL |  | G |  | 0.39 |  | BARG |  | 560 | AMB | degC | 3.43 | BARG | F.V | 650 |  | degC |  | m/s |  | kg/m3 |  | cP

## CV
Rev | Name | Case | Old Tag Name | Logically deleted from the project | Inst_Type_Code | Seq No | Suffix | Qty | P&ID No | Service | Inst Type Desc | Line Size | Plant Connection (Text) | Line Spec | Fluid Code | Fluid Name | Phase | OP Max | OP Nor | OP Min | OP UOM | OT Max | OT Nor | OT Min | OT UOM | DP (Int) | DP (Int) UOM | DP (FV) | DT Hot | DT Cold | DT UOM | Flow Rate Max | Flow Rate Nor | Flow Rate Min | Flow Rate UOM | Pressure Loss Maximum | Pressure Loss Normal | Press Loss UOM | Density | Density UOM | Viscosity | Viscosity UOM | MW | CpCv | Comp. Z | Critical_Press | Critical_Press_UOM | Vapor_Press | Vapor_Press_UOM | Flash Percent | UOM for Flash Percent | Shut Off DP | Shut Off DP UOM | Tight Shut Off | Failure Action | Hand Wheel | Remarks-PS
A | FV-3111A |  |  | FALSE | FV | 3111 | A | 1 | B-1-3111A | EE TO HE-3101A |  | 2" |  | C27 | EE |  | V |  | 3.92 |  | BARG |  | 15 | -10 | degC | 34.3233 | BARG | - | 60 | -45 | degC | 173 | 115 |  | Nm3/hr |  | 3.5304 | BAR |  |  | 0.01 | cP | 28.05 | 1.296 | 0.954 | [6 empty] | 34.32 | BAR |  | FC
A | FV-3111B |  |  | FALSE | FV | 3111 | B | 1 | B-1-3111B | EE TO HE-3101B |  | 2" |  | C27 | EE |  | V |  | 3.92 |  | BARG |  | 15 | -10 | degC | 34.3233 | BARG | - | 60 | -45 | degC | 173 | 115 |  | Nm3/hr |  | 3.5304 | BAR |  |  | 0.01 | cP | 28.05 | 1.296 | 0.954 | [6 empty] | 34.32 | BAR |  | FC
F | FV-3121A |  |  | FALSE | FV | 3121 | A | 1 | B-1-3111A | NL TO EH-3102A |  | 4" |  | A50 | NL |  | G |  | 1.96 |  | BARG | 150 | 25 |  | degC | 3.4323 | BARG | - | 400 |  | degC | 435 | 290 |  | Nm3/hr |  | 1.5691 | BAR |  |  | 0.02 | cP | 28.01 | 1.404 | 0.999 | [6 empty] | 3.43 | BAR |  | FO |  | 60% 3D MODEL COMMENT에 따라 변경
F | FV-3121B |  |  | FALSE | FV | 3121 | B | 1 | B-1-3111B | NL TO EH-3102B |  | 4" |  | A50 | NL |  | G |  | 1.96 |  | BARG | 150 | 25 |  | degC | 3.4323 | BARG | - | 400 |  | degC | 435 | 290 |  | Nm3/hr |  | 1.5691 | BAR |  |  | 0.02 | cP | 28.01 | 1.404 | 0.999 | [6 empty] | 3.43 | BAR |  | FO |  | 60% 3D MODEL COMMENT에 따라 변경
F | LV-3703 |  |  | FALSE | LV | 3703 |  | 1 | B-1-3715 | WF TO TW-3701 |  | 1" |  | A50 | WF |  | L |  | 3.92 |  | BARG |  | AMB |  | degC | 6.8647 | BARG | - | 60 |  | degC | 1.71 | 1.50 |  | m3/hr |  | 0.68647 | BAR | 995 | kg/m3 | 0.76 | cP | [5 empty] | 0.05 | BARA |  |  | 6.86 | BAR |  | FC |  | ETW
B | LV-3741 |  |  | FALSE | LV | 3741 |  | 1 | B-1-3741 | WF TO TW-3741 |  | 1" |  | A50 | WF |  | L |  | 3.92 |  | BARG |  | AMB |  | degC | 6.8647 | BARG | - | 60 |  | degC | 1.71 | 1.50 |  | m3/hr |  | 0.68647 | BAR | 995 | kg/m3 | 0.76 | cP | [5 empty] | 0.05 | BARA |  |  | 6.86 | BAR |  | FC |  | ETW
F | PCV-3102A |  |  | FALSE | PCV | 3102 | A | 1 | B-1-3111A | NL TO EH-3102A |  | 1/2" |  | A50 | NL |  | G |  |  |  | BARG |  |  |  | degC |  | BARG |  |  |  | degC | [25 empty] | BY VENDOR SET: 0.049 barg (SET: 0.05 kg/cm2G)
F | PCV-3102B |  |  | FALSE | PCV | 3102 | B | 1 | B-1-3111B | NL TO EH-3102B |  | 1/2" |  | A50 | NL |  | G |  |  |  | BARG |  |  |  | degC |  | BARG |  |  |  | degC | [25 empty] | BY VENDOR SET: 0.049 barg (SET: 0.05 kg/cm2G)
G | PCV-3301A |  |  | TRUE | PCV | 3301 | A | 1 | B-1-3311A | NG TO HP-3301A |  | 1/2" |  | A50 | NG |  | G |  |  |  | BARG |  |  |  | degC |  | BARG |  |  |  | degC | [25 empty] | BY VENDOR SET: 1.96 barg SET : 2.0 kg/cm2G
G | PCV-3301B |  |  | TRUE | PCV | 3301 | B | 1 | B-1-3311B | NG TO HP-3301B |  | 1/2" |  | A50 | NG |  | G |  |  |  | BARG |  |  |  | degC |  | BARG |  |  |  | degC | [25 empty] | BY VENDOR SET: 1.96 barg SET : 2.0 kg/cm2G

## PSV
Rev | Name | Case | Old Tag Name | Logically deleted from the project | Type_Code | Seq No | Suffix | Qty | P&ID No | Service | Inst Type Desc | Inlet Size (ANSI) | Inlet MOC (ANSI) | Outlet Size (ANSI) | Outlet MOC (ANSI) | Plant Connection - Text | Sizing Basis | Fluid Code | Fluid Name | State | Required Capacity | Required Capacity UOM | Press Set | Press UOM | Over Press | Over Press UOM | Constant Back Press | Variable Back Press | Builtup Back Pressure | Total Back Press | :Back_Press_UOM | Temp Relieving | Temp Relieving UOM | MW | Cp/Cv | Compressibility Z | Viscosity | Viscosity UOM | Density | Density UOM | Remarks-PS